appendix 2

Straight Run Requirements

for Flow Metering

Contents

1.0	SCOPE	3

2.0	INSTRUCTION	3

2.1	MAGNETIC FLOW METERS	3

2.2	ANNUBAR, VORTEX, and ORIFICE METERS	3

# SCOPE

The following up and downstream unobstructed straight lengths are required by the Instrument Group for all Magnetic, Annubar, Vortex, and Orifice meters runs. Required Diameters ‘D’ is the nominal pipe size in metric.

# INSTRUCTION

## MAGNETIC FLOW METERS

A straight  run upstream length of 5D minimum is required from the weld of the elbow or tee

regardless of the piping configuration before the elbow or tee.  The downstream run is 3D Minimum to the weld of the next fitting.

The preferred mounting position is in a horizontal line fully flooded (See Note1)

## ANNUBAR, VORTEX, and ORIFICE METERS

Where the upstream elbow is more than from the previous elbow or tee the upstream straight run from the weld of the elbow to the flow meter is 20D minimum

Where the upstream elbow is less than 10D from the previous elbow or tee in the same plane, the upstream straight run from the weld of the elbow to the flow  meter is 25D minimum.

Where the upstream elbow is lees than  10D from the previous elbow or tee in a different plane, or the last upstream component is a globe valve, the upstream straight run from the weld of the elbow or valve flange to the flow meter is 40D minimum.

For annubars in gas or vapor systems the flow element should be mounted in the horizontal position to avoid any potential error caused by any condensed liquid in the pipe.  In liquid lines preferred mounting position is in a horizontal line with the line fully flooded (see Note1)

The downstream length is 5D minimum in all cases.

NOTES:

1.   Horizontal liquid lines at high points of piping systems do not usually run full of liquid.  Where the accuracy of a meter is critical to the Instrument Group and would be improved by the meter being fully flooded a note will be added to the P&ID.

Only in cases where this note is present and the piping configuration is such that a LIQUID meter run is placed in the horizontal at the high point of the piping system, a “gooseneck” shall be created at the first downstream  down-turned elbow to keep the line fully flooded. The gooseneck will consist of two vertical 45 elbows welded together and a short horizontal  (150mm) pup piece with a valve vent immediately before the down-turned elbow. As a second choice  the meter run can be placed in an upward flowing vertical pipe run, but NEVER in a downward flowing vertical run.   These requirements do not apply to gas or vapor systems.

- In any situation where these straight lengths cannot be achieved by good piping design the Instrument Group must be consulted on the use of flow conditioner devises (e.g. straightening vanes).