## 150 lb.
150# RF PIPING DIMENSIONS
SIZE | PIPE O.D. | WN FLG | OD FLG | 45 ELL | TEE | REDUCER | CAP | LR ELL & WN FLG | TEE & WN FLG | 45 ELL & WN FLG | GATE VALVE |  |  | CHECK VALVE | GLOBE VALVE |  |  | BUTTERFLY VALVE (1) | WAFER CHECK VALVE (2) | BALL VALVE (3) | [6 empty] | SIZE | NO. BOLTS | STUD BOLT SIZE
[20 empty] | FULL PORT | RED. PORT | VALVE TO HW (FB) | HW OFFSET (FB) | HW PROJ (FB) | HW OD (FB) | LEVER LENGTH (FB) |  |  | DIAMETER | LENGTH (4)
|  | A | B | C | D | E | F | G | H | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
1" | 1.3125 | A: 2.1875; B: 4.25; C: 7/8; D: 1.5; E: 2; F: 1.5; G: 3.6875; H: 3.6875; J: 3.0625; FULL PORT T: 5; LEVER LENGTH (FB) Z: 9 | 1" | 4 | 0.5 | 2.75
1 1/2" | 1.875 | A: 2.4375; B: 5; C: 1.125; D: 2.25; E: 2.5; F: 1.5; G: 4.6875; H: 4.6875; J: 3.5625; FULL PORT T: 6.5; LEVER LENGTH (FB) Z: 15 | 1 1/2" | 4 | 0.5 | 3
2" | 2.375 | 2.5 | 6 | 1.375 | 2.5 | 3 | 1.5 | 5.5 | 5 | 3.875 | 7 | 15.75 | 8 | 8 | 8 | 13.75 | 8 |  | 2.375 | 7 | 7 | 4.75 |  |  |  | 23 | 2" | 4 | 0.625 | 3.25
2 1/2" | 2.875 | 2.75 | 7 | 1.75 | 3 | 3.5 | 1.5 | 6.5 | 5.75 | 4.5 | 7.5 | 16.5 | 8 | 8.5 | 8.5 | 14.5 | 8 |  | 2.625 | [7 empty] | 2 1/2" | 4 | 0.625 | 3.5
3" | 3.5 | 2.75 | 7.5 | 2 | 3.375 | 3.5 | 2 | 7.25 | 6.125 | 4.75 | 8 | 20.75 | 9 | 9.5 | 9.5 | 16.5 | 9 | 1.875 | 2.875 | 8 | 8 | 7.0625 | 3.125 | 10.0625 | 17.125 | 33 | 3" | 4 | 0.625 | 3.75
4" | 4.5 | 3 | 9 | 2.5 | 4.125 | 4 | 2.5 | 9 | 7.125 | 5.5 | 9 | 25.75 | 10 | 11.5 | 11.5 | 19.75 | 10 | 2.125 | 2.875 | 9 | 9 | 8 | 3.125 | 10.0625 | 17.125 | 44 | 4" | 8 | 0.625 | 3.75
6" | 6.625 | 3.5 | 11 | 3.75 | 5.625 | 5.5 | 3.5 | 12.5 | 9.125 | 7.25 | 10.5 | 35.25 | 14 | 14 | 16 | 24.5 | 12 | 2.25 | 3.875 | 15.5 | 10.5 | 10.8125 | 5 | 11.5 | 24 |  | 6" | 8 | 0.75 | 4
8" | 8.625 | 4 | 13.5 | 5 | 7 | 6 | 4 | 16 | 11 | 9 | 11.5 | 44 | 16 | 19.5 | 19.5 | 26 | 16 | 2.5 | 5 | 18 | 18 | 12.625 | 5 | 11.5 | 24 |  | 8" | 8 | 0.75 | 4.25
10" | 10.75 | 4 | 16 | 6.25 | 8.5 | 7 | 5 | 19 | 12.5 | 10.25 | 13 | 52.5 | 18 | 24.5 |  |  |  | 2.8125 | 5.75 | 21 | 21 | 15.625 | 3.6875 | 18.9375 | 30.25 |  | 10" | 12 | 0.875 | 4.75
12" | 12.75 | 4.5 | 19 | 7.5 | 10 | 8 | 6 | 22.5 | 14.5 | 12 | 14 | 60.5 | 18 | 27.5 |  |  |  | 3.1875 | 7.125 | 24 | 24 | 17.375 | 3.6875 | 18.9375 | 30.25 |  | 12" | 12 | 0.875 | 4.75
14" | 14 | 5 | 21 | 8.75 | 11 | 13 | 6.5 | 26 | 16 | 13.75 | 15 | 70.25 | 22 | 35 |  |  |  | 3.625 | 7.25 | 27 | 27 | 18.4375 | 3.6875 | 18.9375 | 30.25 |  | 14" | 12 | 1 | 5.25
16" | 16 | 5 | 23.5 | 10 | 12 | 14 | 7 | 29 | 17 | 15 | 16 | 79.75 | 24 | 39 |  |  |  | 4 | 7.5 | 30 | 30 | 20.125 | 3.6875 | 18.9375 | 39 |  | 16" | 16 | 1 | 5.5
18" | 18 | 5.5 | 25 | 11.25 | 13.5 | 15 | 8 | 32.5 | 19 | 16.75 | 17 | 89 | 27 |  |  |  |  | 4.5 | 8 | 34 |  | 24.8125 | 4.875 | 21.5 | 30.25 |  | 18" | 16 | 1.125 | 6
20" | 20 | 5.6875 | 27.5 | 12.5 | 15 | 20 | 9 | 35.6875 | 20.6875 | 18.1875 | 18 | 97.25 | 30 |  |  |  |  | 5 | 8.625 | 36 | 36 | 25.375 | 4.875 | 21.5 | 39 |  | 20" | 20 | 1.125 | 6.25
24" | 24 | 6 | 32 | 15 | 17 | 20 | 10.5 | 42 | 23 | 21 | 20 | 112.75 | 30 |  |  |  |  | 6.0625 | 8.75 | 42 | 42 | 30.375 | 4.875 | 21.5 | 39 |  | 24" | 20 | 1.25 | 7
26" | 26 | 4.75 | 34.25 | 16 | 19.5 | 24 | 10.5 | 43.75 | 24.25 | 20.75 | [8 empty] | 14 | 45 |  | 34.25 | 5.75 | 31.375 | 30.25 |  | 26" | 24 | 1.25 | 7.25
28" | 28 | 4.9375 | 36.5 | 17.25 | 20.5 | 24 | 10.5 | 46.9375 | 25.4375 | 22.1875 | [8 empty] | 12 | 49 |  | 35.125 | 5.75 | 31.375 | 30.25 |  | 28" | 28 | 1.25 | 7.25
30" | 30 | 5.375 | 38.75 | 18.5 | 22 | 24 | 10.5 | 50.375 | 27.375 | 23.875 | [7 empty] | 6.25 | 12 | 51 |  | 37.125 | 5.75 | 31.375 | 30.25 |  | 30" | 28 | 1.25 | 7.5
36" | 36 | 6.1875 | 46 | 22.25 | 26.5 | 24 | 10.5 | 60.1875 | 32.6875 | 28.4375 | [7 empty] | 7 | 14.5 | 60 |  | 42.875 | 16 | 37.25 | 30.25 |  | 36" | 32 | 1.5 | 8.5
42" | 42 | A: 6.75; B: 53; C: 26; D: 30; E: 24; F: 12; G: 69.75; H: 36.75; J: 32.75; R: 9; S: 17 | 42" | 36 | 1.5 | 9
(1) Posi-seal Butterfly Valves |  | C: CALC. BOX
(2) Crane Duo-Chek II
(3) TK Ball Valves
(4) Length does not include crowns

## 300 lb.
300# RF PIPING DIMENSIONS
SIZE | PIPE O.D. | WN FLG | OD FLG | 45 ELL | TEE | REDUCER | CAP | LR ELL & WN FLG | TEE & WN FLG | 45 ELL & WN FLG | GATE VALVE |  |  | CHECK VALVE | GLOBE VALVE |  |  | WAFER BUTTERFLY VALVE (1) | WAFER CHECK VALVE (2) | BALL VALVE (3) | [6 empty] | SIZE | NO. BOLTS | STUD BOLT SIZE
[20 empty] | FULL PORT | RED. PORT | VALVE TO HW (FB) | HW OFFSET (FB) | HW PROJ (FB) | HW OD (FB) | LEVER LENGTH (FB) |  |  | DIAMETER | LENGTH (4)
|  | A | B | C | D | E | F | G | H | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
1" | 1.3125 | A: 2.4375; B: 4.875; C: 7/8; D: 1.5; E: 2; F: 1.5; G: 3.9375; H: 3.9375; J: 3.3125; FULL PORT T: 6.5 | 1" | 4 | 0.625 | 3.25
1 1/2" | 1.875 | A: 2.6875; B: 6.125; C: 1.125; D: 2.25; E: 2.5; F: 1.5; G: 4.9375; H: 4.9375; J: 3.8125; K: 7.5; L: 16.75; M: 8; FULL PORT T: 7.5 | 1 1/2" | 4 | 0.75 | 3.75
2" | 2.375 | 2.75 | 6.5 | 1.375 | 2.5 | 3 | 1.5 | 5.75 | 5.25 | 4.125 | 8.5 | 18 | 8 | 10.5 | 10.5 | 17.75 | 9 |  | 2.375 | 8.5 | 8.5 | 4.0625 |  |  |  | 23 | 2" | 8 | 0.625 | 3.5
2 1/2" | 2.875 | 3 | 7.5 | 1.75 | 3 | 3.5 | 1.5 | 6.75 | 6 | 4.75 | 9.5 | 19 | 8 | 11.5 | 11.5 | 19 | 10 |  | 2.625 | [7 empty] | 2 1/2" | 8 | 0.75 | 4
3" | 3.5 | 3.125 | 8.25 | 2 | 3.375 | 3.5 | 2 | 7.625 | 6.5 | 5.125 | 11.125 | 23.25 | 9 | 12.5 | 12.5 | 20.5 | 10 | 1.875 | 2.875 | 11.125 | 11.125 | 7.0625 | 3.125 | 10.0625 | 17.125 | 33 | 3" | 8 | 0.75 | 4.25
4" | 4.5 | 3.375 | 10 | 2.5 | 4.125 | 4 | 2.5 | 9.375 | 7.5 | 5.875 | 12 | 28.25 | 10 | 14 | 14 | 24.75 | 14 | 2.125 | 2.875 | 12 | 12 | 8 | 3.125 | 10.0625 | 17.125 | 44 | 4" | 8 | 0.75 | 4.5
6" | 6.625 | 3.875 | 12.5 | 3.75 | 5.625 | 5.5 | 3.5 | 12.875 | 9.5 | 7.625 | 15.875 | 38.5 | 14 | 17.5 | 17.5 | 29.75 | 18 | 2.3125 | 3.875 | 15.875 | 15.875 | 10.8125 | 5 | 11.5 | 24 |  | 6" | 12 | 0.75 | 5
8" | 8.625 | 4.375 | 15 | 5 | 7 | 6 | 4 | 16.375 | 11.375 | 9.375 | 16.5 | 47 | 16 | 21 | 22 | 36.5 | 24 | 2.875 | 5 | 19.75 | 19.75 | 12.5 | 5 | 11.5 | 24 |  | 8" | 12 | 0.875 | 5.5
10" | 10.75 | 4.625 | 17.5 | 6.25 | 8.5 | 7 | 5 | 19.625 | 13.125 | 10.875 | 18 | 56.5 | 20 | 24.5 |  |  |  | 3.3125 | 5.75 | 22.375 | 22.375 | 15.625 | 3.6875 | 18.9375 | 30.25 |  | 10" | 16 | 1 | 6.25
12" | 12.75 | 5.125 | 20.5 | 7.5 | 10 | 8 | 6 | 23.125 | 15.125 | 12.625 | 19.75 | 64.25 | 20 | 28 |  |  |  | 3.625 | 7.125 | 25.5 | 25.5 | 16.8125 | 3.6875 | 18.9375 | 30.25 |  | 12" | 16 | 1.125 | 6.75
14" | 14 | 5.625 | 23 | 8.75 | 11 | 13 | 6.5 | 26.625 | 16.625 | 14.375 | 30 | 75.25 | 27 |  |  |  |  | 4.625 | 8.75 | 30 | 30 | 18.4375 | 3.6875 | 18.9375 | 30.25 |  | 14" | 20 | 1.125 | 7
16" | 16 | 5.75 | 25.5 | 10 | 12 | 14 | 7 | 29.75 | 17.75 | 15.75 | 33 | 81 | 27 |  |  |  |  | 5.25 | 9.125 | 33 | 33 | 20.125 | 3.6875 | 18.9375 | 39 |  | 16" | 20 | 1.25 | 7.5
18" | 18 | 6.25 | 28 | 11.25 | 13.5 | 15 | 8 | 33.25 | 19.75 | 17.5 | 36 | 91.5 | 30 |  |  |  |  | 5.875 | 10.375 | 36 |  | 24.8125 | 4.875 | 21.5 | 39 |  | 18" | 24 | 1.25 | 7.75
20" | 20 | 6.375 | 30.5 | 12.5 | 15 | 20 | 9 | 36.375 | 21.375 | 18.875 | 39 | 99.75 | 36 |  |  |  |  | 6.25 | 11.5 | 39 | 39 | 16.5 | 4.875 | 21.5 | 39 |  | 20" | 24 | 1.25 | 8.25
24" | 24 | 6.625 | 36 | 15 | 17 | 20 | 10.5 | 42.625 | 23.625 | 21.625 | 45 | 120.5 | 36 |  |  |  |  | 7 | 12.5 | 45 | 45 | 29.3125 | 4.875 | 21.5 | 39 |  | 24" | 24 | 1.5 | 9.25
26" | 26 | 7.25 | 38.25 | 16 | 19.5 | 24 | 10.5 | 46.25 | 26.75 | 23.25 | [8 empty] | 14 | 49 |  | 34.25 | 5.75 | 31.375 | 30.25 |  | 26" | 28 | 1.625 | 10.25
28" | 28 | A: 7.75; B: 40.75; C: 17.25; D: 20.5; E: 24; F: 10.5; G: 49.75; H: 28.25; J: 25; FULL PORT T: 53; VALVE TO HW (FB) V: 35.125; HW OFFSET (FB) W: 5.75; HW PROJ (FB) X: 31.375; HW OD (FB) Y: 30.25 | 28" | 28 | 1.625 | 10.75
30" | 30 | 8.25 | 43 | 18.5 | 22 | 24 | 10.5 | 53.25 | 30.25 | 26.75 | [7 empty] | 9.5 | 14.5 | 55 |  | 37.125 | 5.75 | 31.375 | 30.25 |  | 30" | 28 | 1.75 | 11.5
36" | 36 | 9.5 | 50 | 22.25 | 26.5 | 24 | 10.5 | 63.5 | 36 | 31.75 | [7 empty] | 10.75 | 19 | 68 |  | 40.875 | 16 | 37.25 | 30.25 |  | 36" | 32 | 2 | 13
42" | 42 | A: 7.875; B: 50.75; C: 26; D: 30; E: 24; F: 12; G: 70.875; H: 37.875; J: 33.875; S: 22.375 | 42" | 36 | 2 | 14
(1) Posi-seal Butterfly Valves |  | C: CALC. BOX
(2) Crane Duo-Chek II
(3) TK Ball Valves
(4) Length does not include crowns

## 600 lb.
600# RF PIPING DIMENSIONS
SIZE | PIPE O.D. | WN FLG | OD FLG | 45 ELL | TEE | REDUCER | CAP | LR ELL & WN FLG | TEE & WN FLG | 45 ELL & WN FLG | GATE VALVE |  |  | CHECK VALVE | GLOBE VALVE |  |  | BUTTERFLY VALVE (1) | WAFER CHECK VALVE (2) | BALL VALVE (3) | [6 empty] | SIZE | NO. BOLTS | STUD BOLT SIZE
[20 empty] | FULL PORT | RED. PORT | VALVE TO HW | HW OFFSET | HW PROJ | HW OD | LEVER LENGTH |  |  | DIAMETER | LENGTH (4)
|  | A | B | C | D | E | F | G | H | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
1" | 1.3125 | A: 2.6875; B: 4.875; C: 7/8; D: 1.5; E: 2; F: 1.5; G: 4.1875; H: 4.1875; J: 3.5625; FULL PORT T: 8.5; VALVE TO HW V: 3.125; LEVER LENGTH Z: 9 | 1" | 4 | 0.625 | 3.75
1 1/2" | 1.875 | A: 3; B: 6.125; C: 1.125; D: 2.25; E: 2.5; F: 1.5; G: 5.25; H: 5.25; J: 4.125; N: 9.5; FULL PORT T: 9.5; VALVE TO HW V: 4.75; LEVER LENGTH Z: 15 | 1 1/2" | 4 | 0.75 | 4.25
2" | 2.375 | 3.125 | 6.5 | 1.375 | 2.5 | 3 | 1.5 | 6.125 | 5.625 | 4.5 | 11.5 | 18.25 | 8 | 11.5 | 11.5 | 19 | 10 |  | 2.375 | 11.5 | 11.5 | 5.8125 |  |  |  | 23 | 2" | 8 | 0.625 | 4.25
2 1/2" | 2.875 | 3.375 | 7.5 | 1.75 | 3 | 3.5 | 1.5 | 7.125 | 6.375 | 5.125 | 13 | 22.25 | 9 | 13 | 13 | 21.25 | 12 |  | 2.625 | [7 empty] | 2 1/2" | 8 | 0.75 | 4.75
3" | 3.5 | 3.5 | 8.25 | 2 | 3.375 | 3.5 | 2 | 8 | 6.875 | 5.5 | 14 | 25.75 | 10 | 14 | 14 | 23.5 | 12 | 1.8125 | 2.875 | 14 | 14 | 7.0625 | 3.125 | 10.0625 | 17.125 | 33 | 3" | 8 | 0.75 | 5
4" | 4.5 | 4.25 | 10.75 | 2.5 | 4.125 | 4 | 2.5 | 10.25 | 8.375 | 6.75 | 17 | 31.5 | 14 | 17 | 17 | 27.5 | 18 | 2.375 | 3.125 | 17 | 17 | 8 | 3.125 | 10.625 | 17.125 | 44 | 4" | 8 | 0.875 | 5.75
6" | 6.625 | 4.875 | 14 | 3.75 | 5.625 | 5.5 | 3.5 | 13.875 | 10.5 | 8.625 | 22 | 42.75 | 20 | 22 | 22 | 35 | 24 | 2.875 | 5.375 | 22 | 22 | 10.8125 | 5 | 11.5 | 24 |  | 6" | 12 | 1 | 6.75
8" | 8.625 | 5.5 | 16.5 | 5 | 7 | 6 | 4 | 17.5 | 12.5 | 10.5 | 26 | 52.25 | 24 | 26 |  |  |  | 3.5 | 6.5 | 26 | 26 | 14 | 3.6875 | 18.9375 | 30.25 |  | 8" | 12 | 1.125 | 7.75
10" | 10.75 | 6.25 | 20 | 6.25 | 8.5 | 7 | 5 | 21.25 | 14.75 | 12.5 | 31 | 62.25 | 27 | 31 |  |  |  | 4.5 | 8.375 | 31 | 31 | 15.5 | 3.6875 | 18.9375 | 30.25 |  | 10" | 16 | 1.25 | 8.5
12" | 12.75 | 6.375 | 22 | 7.5 | 10 | 8 | 6 | 24.375 | 16.375 | 13.875 | 33 | 70 | 27 | 33 |  |  |  | 5.5 | 9 | 33 | 33 | 17.4375 | 3.6875 | 18.9375 | 30.25 |  | 12" | 20 | 1.25 | 8.75
14" | 14 | 6.75 | 23.75 | 8.75 | 11 | 13 | 6.5 | 27.75 | 17.75 | 15.5 | 35 | 77.25 | 30 |  |  |  |  | 6.25 | 10.75 | 35 | 35 | 21.5 | 4.875 | 21.5 | 39 |  | 14" | 20 | 1.375 | 9.25
16" | 16 | 7.25 | 27 | 10 | 12 | 14 | 7 | 31.25 | 19.25 | 17.25 | 39 | 83.75 | 30 |  |  |  |  | 7 | 12 | 39 | 39 | 20.0625 | 4.875 | 21.5 | 39 |  | 16" | 20 | 1.5 | 10
18" | 18 | 7.5 | 29.25 | 11.25 | 13.5 | 15 | 8 | 34.5 | 21 | 18.75 | 43 | 93.75 | 36 |  |  |  |  | 7.75 | 14.25 | 43 | 43 | 25.625 | 7.75 | 28 | 30.25 |  | 18" | 20 | 1.625 | 10.75
20" | 20 | 7.75 | 32 | 12.5 | 15 | 20 | 9 | 37.75 | 22.75 | 20.25 | 47 | 104.5 | 36 |  |  |  |  | 9 | 14.5 | 47 | 47 | 27.375 | 7.75 | 28 | 30.25 |  | 20" | 24 | 1.625 | 11.5
24" | 24 | 8.25 | 37 | 15 | 17 | 20 | 10.5 | 44.25 | 25.25 | 23.25 | 55 | 126 | 42 |  |  |  |  | 9 | 17.25 | 55 | 55 | 31.375 | 9.75 | 30 | 30.25 |  | 24" | 24 | 1.875 | 13
(1) Posi-seal Butterfly Valves |  | C: CALC. BOX
(2) Crane Duo-Chek II
(3) TK Ball Valves
(4) Length does not include crowns

## 900 lb.
900# RF PIPING DIMENSIONS
SIZE | PIPE O.D. | WN FLG | OD FLG | 45 ELL | TEE | REDUCER | CAP | LR ELL & WN FLG | TEE & WN FLG | 45 ELL & WN FLG | GATE VALVE |  |  | CHECK VALVE | GLOBE VALVE |  |  | WAFER BUTTERFLY VALVE (1) | WAFER CHECK VALVE (2) | BALL VALVE (3) | [6 empty] | SIZE | NO. BOLTS | STUD BOLT SIZE
[20 empty] | FULL PORT | RED. PORT | VALVE TO HW (FB) | HW OFFSET (FB) | HW PROJ (FB) | HW OD (FB) | LEVER LENGTH FB) |  |  | DIAMETER | LENGTH (4)
|  | A | B | C | D | E | F | G | H | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
1" | 1.3125 | A: 3.125; B: 5.875; C: 7/8; D: 1.5; E: 2; F: 1.5; G: 4.625; H: 4.625; J: 4; FULL PORT T: 10; LEVER LENGTH FB) Z: 9 | 1" | 4 | 0.875 | 5
1 1/2" | 1.875 | A: 3.5; B: 7; C: 1.125; D: 2.25; E: 2.5; F: 1.5; G: 5.75; H: 5.75; J: 4.625; FULL PORT T: 12; LEVER LENGTH FB) Z: 15 | 1 1/2" | 4 | 1 | 5.5
2" | 2.375 | A: 4.25; B: 8.5; C: 1.375; D: 2.5; E: 3; F: 1.5; G: 7.25; H: 6.75; J: 5.625; R: 2.75; S: 2.75; FULL PORT T: 14.5; RED. PORT U: 14.5; LEVER LENGTH FB) Z: 33 | 2" | 8 | 0.875 | 5.75
2 1/2" | 2.875 | A: 4.375; B: 9.625; C: 1.75; D: 3; E: 3.5; F: 1.5; G: 8.125; H: 7.375; J: 6.125; R: 3.25; S: 3.25 | 2 1/2" | 8 | 1 | 6.25
3" | 3.5 | 4.25 | 9.5 | 2 | 3.375 | 3.5 | 2 | 8.75 | 7.625 | 6.25 | 15 | 27.25 | 12 | 15 | 15 | 24 | 12 | 3.25 | 3.25 | 15 | 15 | 7.0625 | 3.125 | 10.0625 | 17.125 | 33 | 3" | 8 | 0.875 | 5.75
4" | 4.5 | 4.75 | 11.5 | 2.5 | 4.125 | 4 | 2.5 | 10.75 | 8.875 | 7.25 | 18 | 31.5 | 14 | 18 | 18 | 29.5 | 20 | 4 | 4 | 18 | 18 | 9.5625 | 5 | 11.5 | 24 | 44 | 4" | 8 | 1.125 | 6.75
6" | 6.625 | 5.75 | 15 | 3.75 | 5.625 | 5.5 | 3.5 | 14.75 | 11.375 | 9.5 | 24 | 42.75 | 20 | 24 | 24 | 37.75 | 27 | 6.25 | 6.25 | 24 | 24 | 10.8125 | 5 | 11.5 | 24 |  | 6" | 12 | 1.125 | 7.75
8" | 8.625 | 6.625 | 18.5 | 5 | 7 | 6 | 4 | 18.625 | 13.625 | 11.625 | 29 | 52.5 | 24 | 29 |  |  |  | 8.125 | 8.125 | 29 | 29 | 16 | 3.6875 | 18.9375 | 30.25 |  | 8" | 12 | 1.375 | 8.75
10" | 10.75 | 7.5 | 21.5 | 6.25 | 8.5 | 7 | 5 | 22.5 | 16 | 13.75 | 33 | 62.25 | 27 |  |  |  |  | 9.5 | 9.5 | 33 | 33 | 15.625 | 3.6875 | 18.9375 | 30.25 |  | 10" | 16 | 1.375 | 9.25
12" | 12.75 | 8.125 | 24 | 7.5 | 10 | 8 | 6 | 26.125 | 18.125 | 15.625 | 38 | 73.5 | 30 |  |  |  |  | 11.5 | 11.5 | 38 | 38 | 18.375 | 3.6875 | 18.9375 | 30.25 |  | 12" | 20 | 1.375 | 10
14" | 14 | 8.625 | 25.25 | 8.75 | 11 | 13 | 6.5 | 29.625 | 19.625 | 17.375 | 40.5 | 77.25 | 30 |  |  |  |  | 14 | 14 | 40.5 | 40.5 | 21.5 | 4.875 | 21.5 | 39 |  | 14" | 20 | 1.5 | 10.75
16" | 16 | 8.75 | 27.75 | 10 | 12 | 14 | 7 | 32.75 | 20.75 | 18.75 | 44.5 | 85.75 | 36 |  |  |  |  | 15 1//8 | 15.125 | 44.5 | 44.5 | 20.0625 | 4.875 | 21.5 | 39 |  | 16" | 20 | 1.625 | 11.25
18" | 18 | 9.25 | 31 | 11.25 | 13.5 | 15 | 8 | 36.25 | 22.75 | 20.5 | [7 empty] | 17.75 | 17.75 | 48 |  | 25.8125 | 9.75 | 29 | 30.25 |  | 18" | 20 | 1.875 | 12.75
20" | 20 | 10 | 33.75 | 12.5 | 15 | 20 | 9 | 40 | 25 | 22.5 | [7 empty] | 17.75 | 17.75 | 52 | 52 | 28.875 | 5.75 | 31.375 | 30.25 |  | 20" | 20 | 2 | 13.5
24" | 24 | 11.75 | 41 | 15 | 17 | 20 | 10.5 | 47.75 | 28.75 | 26.75 | [7 empty] | 19.5 | 19.5 | 61 | 61 | 30.9375 | 5.75 | 31.375 | 30.25 |  | 24" | 20 | 2.5 | 17.25
(1) Posi-seal Butterfly Valves |  | C: CALC. BOX
(2) Crane Duo-Chek II
(3) TK Ball Valves
(4) Length does not include crowns

## 1500 lb.
1500# RF PIPING DIMENSIONS
SIZE | PIPE O.D. | WN FLG | OD FLG | 45 ELL | TEE | REDUCER | CAP | LR ELL & WN FLG | TEE & WN FLG | 45 ELL & WN FLG | GATE VALVE |  |  | CHECK VALVE | GLOBE VALVE |  |  | WAFER BUTTERFLY VALVE (1) | WAFER CHECK VALVE (2) | BALL VALVE (3) | [6 empty] | SIZE | NO. BOLTS | STUD BOLT SIZE
[20 empty] | FULL PORT | RED. PORT | VALVE TO HW (FB) | HW OFFSET (FB) | HW PROJ (FB) | HW OD (FB) | LEVER LENGTH FB) |  |  | DIAMETER | LENGTH (4)
|  | A | B | C | D | E | F | G | H | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
1" | 1.3125 | 3.125 | 5.875 | 0.875 | 1.5 | 2 | 1.5 | 4.625 | 4.625 | 4 | 10 | 16 | 8 | [6 empty] | 10 |  | 3.125 |  |  |  | 9 | 1" | 4 | 0.875 | 5
1 1/2" | 1.875 | 3.5 | 7 | 1.125 | 2.25 | 2.5 | 1.5 | 5.75 | 5.75 | 4.625 | 12 | 20 | 9 | 12 | [5 empty] | 12 |  | 5.4062 |  |  |  | 15 | 1 1/2" | 4 | 1 | 5.5
2" | 2.375 | 4.25 | 8.5 | 1.375 | 2.5 | 3 | 1.5 | 7.25 | 6.75 | 5.625 | 14.5 | 22.125 | 10 | 14.5 | 14.5 | 25.125 | 14 |  | 2.75 | 14.5 | 14.5 | 6.5 |  |  |  | 33 | 2" | 8 | 0.875 | 5.75
2 1/2" | 2.875 | 4.375 | 9.625 | 1.75 | 3 | 3.5 | 1.5 | 8.125 | 7.375 | 6.125 | 16.5 | 26.375 | 12 | 16.5 | 16.5 | 28.125 | 18 |  | 3.25 | [7 empty] | 2 1/2" | 8 | 1 | 6.25
3" | 3.5 | 4.875 | 10.5 | 2 | 3.375 | 3.5 | 2 | 9.375 | 8.25 | 6.875 | 18.5 | 28 | 14 | 18.5 | 18.5 | 33.5 | 24 |  | 3.25 | 18.5 | 18.5 | 7.375 | 3.125 | 10.25 | 17.125 | 33 | 3" | 8 | 1.125 | 7
4" | 4.5 | 5.125 | 12.25 | 2.5 | 4.125 | 4 | 2.5 | 11.125 | 9.25 | 7.625 | 21.5 | 33 | 16 | 21.5 |  |  |  |  | 4 | 21.5 | 21.5 | 9.5625 | 5 | 11.5 | 24 | 44 | 4" | 8 | 1.25 | 7.75
6" | 6.625 | 7 | 15.5 | 3.75 | 5.625 | 5.5 | 3.5 | 16 | 12.625 | 10.75 | 27.75 | 47 | 24 | 27.75 |  |  |  |  | 6.25 | 27.75 | 27.75 | 12.5625 | 5 | 18.9375 | 30.25 |  | 6" | 12 | 1.375 | 10.25
8" | 8.625 | 8.625 | 19 | 5 | 7 | 6 | 4 | 20.625 | 15.625 | 13.625 | 32 /34 | 55 | 27 | 32.75 |  |  |  |  | 8.125 | 32.75 | 32.75 | 14.5 | 3.6875 | 18.9375 | 30.25 |  | 8" | 12 | 1.625 | 11.5
10" | 10.75 | 10.25 | 23 | 6.25 | 8.5 | 7 | 5 | 25.25 | 18.75 | 16.5 | [8 empty] | 9.75 | 39 | 39 | 18.875 | 4.875 | 21.5 | 39 |  | 10" | 12 | 1.875 | 13.25
12" | 12.75 | 11.375 | 26.5 | 7.5 | 10 | 8 | 6 | 29.375 | 21.375 | 18.875 | [8 empty] | 12 | 44.5 | 44.5 | 21.6875 | 4.875 | 21.5 | 39 |  | 12" | 16 | 2 | 14.75
14" | 14 | 12 | 29.5 | 8.75 | 11 | 13 | 6.5 | 33 | 23 | 20.75 | [8 empty] | 14 | 49.5 | 49.5 | 23.75 | 9.75 | 29 | 39 |  | 14" | 16 | 2.25 | 16
16" | 16 | 12.5 | 32.5 | 10 | 12 | 14 | 7 | 36.5 | 24.5 | 22.5 | [8 empty] | 15.125 | 54.5 | 54.5 | 25.75 | 9.75 | 29 | 30.25 |  | 16" | 16 | 2.5 | 17.5
18" | 18 | 13.125 | 36 | 11.25 | 13.5 | 15 | 8 | 40.125 | 26.625 | 24.375 | [8 empty] | 18.4375 | 60.5 |  | 30.5 | 5.75 | 31.375 | 30.25 |  | 18" | 16 | 2.75 | 19.5
20" | 20 | 14.25 | 38.75 | 12.5 | 15 | 20 | 9 | 44.25 | 29.25 | 26.75 | [8 empty] | 21 | 65.5 | 65.5 | 31.25 | 5.75 | 31.375 | 30.25 |  | 20" | 16 | 3 | 21.5
24" | 24 | 16.25 | 46 | 15 | 17 | 20 | 10.5 | 52.25 | 33.25 | 31.25 | [8 empty] | 22 | 76.5 | 76.5 | 37.875 | 16 | 37.25 | 30.25 |  | 24" | 16 | 3.5 | 24.5
(1) |  | C: CALC. BOX
(2) Crane Duo-Chek II
(3) TK Ball Valves
(4) Length does not include crowns

## 900 lb. RJT
900# RTJ PIPING DIMENSIONS
SIZE | PIPE O.D. | WN FLG | OD FLG | 45 ELL | TEE | REDUCER | CAP | LR ELL & WN FLG | TEE & WN FLG | 45 ELL & WN FLG | GATE VALVE |  |  | CHECK VALVE | GLOBE VALVE |  |  | WAFER BUTTERFLY VALVE (1) | WAFER CHECK VALVE (2) | BALL VALVE (3) | [6 empty] | SIZE | NO. BOLTS | STUD BOLT SIZE |  | RING INFO.
[20 empty] | FULL PORT | RED. PORT | VALVE TO HW (FB) | HW OFFSET (FB) | HW PROJ (FB) | HW OD (FB) | LEVER LENGTH FB) |  |  | DIAMETER | LENGTH (4) | RING NO. | GAP
|  | A | B | C | D | E | F | G | H | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
1" | 1.3125 | A: 3.125; B: 5.875; C: 7/8; D: 1.5; E: 2; F: 1.5; G: 4.625; H: 4.625; J: 4; FULL PORT T: 10; LEVER LENGTH FB) Z: 9 | 1" | 4 | 0.875 | 5 | R-16 | 0.15625
1 1/2" | 1.875 | A: 3.5; B: 7; C: 1.125; D: 2.25; E: 2.5; F: 1.5; G: 5.75; H: 5.75; J: 4.625; FULL PORT T: 12; LEVER LENGTH FB) Z: 15 | 1 1/2" | 4 | 1 | 5.5 | R-20 | 0.15625
2" | 2.375 | 4.3125 | 8.5 | 1.375 | 2.5 | 3 | 1.5 | 7.3125 | 6.8125 | 5.6875 |  |  |  | 14.625 | 14.5 | 23 | 13.75 |  |  | 14.625 | 14.625 |  |  |  |  | 33 | 2" | 8 | 0.875 | 5.75 | R-24 | 0.125
2 1/2" | 2.875 | A: 4.4375; B: 9.625; C: 1.75; D: 3; E: 3.5; F: 1.5; G: 8.1875; H: 7.4375; J: 6.1875; N: 16.625; O: 16.5; P: 24.5; Q: 15.5 | 2 1/2" | 8 | 1 | 6.25 | R-27 | 0.125
3" | 3.5 | 4.3125 | 9.5 | 2 | 3.375 | 3.5 | 2 | 8.8125 | 7.6875 | 6.3125 | 15.125 | 27.25 | 12 | 15.125 | 15.125 | 24 | 12 |  |  | 15.125 | 15.125 | 7.0625 | 3.125 | 10.0625 | 17.125 | 33 | 3" | 8 | 0.875 | 6 | R-31 | 0.15625
4" | 4.5 | 4.8125 | 11.5 | 2.5 | 4.125 | 4 | 2.5 | 10.8125 | 8.9375 | 7.3125 | 18.125 | 31.5 | 14 | 18.125 | 18.125 | 29.5 | 20 |  |  | 18.125 | 18.125 | 9.5625 | 5 | 11.5 | 24 | 44 | 4" | 8 | 1.125 | 7 | R-37 | 0.15625
6" | 6.625 | 5.8125 | 15 | 3.75 | 5.625 | 5.5 | 3.5 | 14.8125 | 11.4375 | 9.5625 | 24.125 | 42.75 | 20 | 24.125 | 24.125 | 37.75 | 27 |  |  | 24.125 | 24.125 | 10.8125 | 5 | 11.5 | 24 |  | 6" | 12 | 1.125 | 7.75 | R-45 | 0.15625
8" | 8.625 | 6.6875 | 18.5 | 5 | 7 | 6 | 4 | 18.6875 | 13.6875 | 11.6875 | 29.125 | 52.5 | 24 | 29.125 | [5 empty] | 29.125 | 29.125 | 16 | 3.6875 | 18.9375 | 30.25 |  | 8" | 12 | 1.375 | 9 | R-49 | 0.15625
10" | 10.75 | 7.5625 | 21.5 | 6.25 | 8.5 | 7 | 5 | 22.5625 | 16.0625 | 13.8125 | 33.125 | 62.25 | 27 | [6 empty] | 33.125 | 33.125 | 15.625 | 3.6875 | 18.9375 | 30.25 |  | 10" | 16 | 1.375 | 9.5 | R-53 | 0.15625
12" | 12.75 | 8.1875 | 24 | 7.5 | 10 | 8 | 6 | 26.1875 | 18.1875 | 15.6875 | 38.125 | 73.5 | 30 | [6 empty] | 38.125 | 38.125 | 18.375 | 3.6875 | 18.9375 | 30.25 |  | 12" | 20 | 1.375 | 10.25 | R-57 | 0.15625
14" | 14 | 8.8125 | 25.25 | 8.75 | 11 | 13 | 6.5 | 29.8125 | 19.8125 | 17.5625 | 40.625 | 77.25 | 30 | [6 empty] | 40.875 | 40.875 | 21.5 | 4.875 | 21.5 | 39 |  | 14" | 20 | 1.5 | 11.25 | R-62 | 0.15625
16" | 16 | 8.9375 | 27.75 | 10 | 12 | 14 | 7 | 32.9375 | 20.9375 | 18.9375 | 44.625 | 85.75 | 36 | [6 empty] | 44.5 | 44.5 | 20.0625 | 4.875 | 21.5 | 39 |  | 16" | 20 | 1.625 | 11.75 | R-66 | 0.15625
18" | 18 | C: 11.25; D: 13.5; E: 15; F: 8; G: 36.5; H: 23; J: 20.75; FULL PORT T: 48.5; VALVE TO HW (FB) V: 25.8125; HW OFFSET (FB) W: 9.75; HW PROJ (FB) X: 29; HW OD (FB) Y: 30.25 | 18" | 20 | 1.875 | 13.5 | R-70 | 0.1875
20" | 20 | 10.25 | 33.75 | 12.5 | 15 | 20 | 9 | 40.25 | 25.25 | 22.75 | [9 empty] | 52.5 | 52.5 | 28.875 | 5.75 | 31.375 | 30.25 |  | 20" | 20 | 2 | 14.25 | R-74 | 0.1875
24" | 24 | 12.125 | 41 | 15 | 17 | 20 | 10.5 | 48.125 | 29.125 | 27.125 | [9 empty] | 61.75 | 61.75 | 30.9375 | 5.75 | 31.375 | 30.25 |  | 24" | 20 | 2.5 | 17.75 | R-78 | 0.21875
(1) |  | C: CALC. BOX
(2)
(3) TK Ball Valves
(4) Length does not include crowns

## 1500 lb. RJT
1500# RTJ PIPING DIMENSIONS
SIZE | PIPE O.D. | WN FLG | OD FLG | 45 ELL | TEE | REDUCER | CAP | LR ELL & WN FLG | TEE & WN FLG | 45 ELL & WN FLG | GATE VALVE |  |  | CHECK VALVE | GLOBE VALVE |  |  | WAFER BUTTERFLY VALVE (1) | WAFER CHECK VALVE (2) | BALL VALVE (3) | [6 empty] | SIZE | NO. BOLTS | STUD BOLT SIZE |  | RING INFO.
[20 empty] | FULL PORT | RED. PORT | VALVE TO HW (FB) | HW OFFSET (FB) | HW PROJ (FB) | HW OD (FB) | LEVER LENGTH FB) |  |  | DIAMETER | LENGTH (4) | RING NO. | GAP
|  | A | B | C | D | E | F | G | H | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
1" | 1.3125 | 3.125 | 5.875 | 0.875 | 1.5 | 2 | 1.5 | 4.625 | 4.625 | 4 | 10.125 | 16 | 8 | [6 empty] | 10 |  | 3.125 |  |  |  | 9 | 1" | 4 | 0.875 | 5 | R-16 | 0.15625
1 1/2" | 1.875 | 3.5 | 7 | 1.125 | 2.25 | 2.5 | 1.5 | 5.75 | 5.75 | 4.625 | 12.125 | 20 | 9 | 12.125 | [5 empty] | 12 |  | 5.4062 |  |  |  | 15 | 1 1/2" | 4 | 1 | 5.5 | R-20 | 0.15625
2" | 2.375 | 4.3125 | 8.5 | 1.375 | 2.5 | 3 | 1.5 | 7.3125 | 6.8125 | 5.6875 | 14.625 | 22.125 | 10 | 14.625 | 14.5 | 25.125 | 14 |  |  | 14.625 | 14.625 | 6.5 |  |  |  | 33 | 2" | 8 | 0.875 | 5.75 | R-24 | 0.125
2 1/2" | 2.875 | 4.4375 | 9.625 | 1.75 | 3 | 3.5 | 1.5 | 8.1875 | 7.4375 | 6.1875 | 16.625 | 26.375 | 12 | 16.625 | 16.5 | 28.125 | 18 | [9 empty] | 2 1/2" | 8 | 1 | 6.25 | R-27 | 0.125
3" | 3.5 | 4.9375 | 10.5 | 2 | 3.375 | 3.5 | 2 | 9.4375 | 8.3125 | 6.9375 | 18.625 | 28 | 14 | 18.625 | 18.5 | 33.5 | 24 |  |  | 18.625 | 18.625 | 7.375 | 3.125 | 10.25 | 17.125 | 33 | 3" | 8 | 1.125 | 7 | R-35 | 0.125
4" | 4.5 | 5.1875 | 12.25 | 2.5 | 4.125 | 4 | 2.5 | 11.1875 | 9.3125 | 7.6875 | 21.625 | 33 | 16 | 21.625 | [5 empty] | 21.625 | 21.625 | 9.5625 | 5 | 11.5 | 24 | 44 | 4" | 8 | 1.25 | 7.75 | R-39 | 0.125
6" | 6.625 | 7.125 | 15.5 | 3.75 | 5.625 | 5.5 | 3.5 | 16.125 | 12.75 | 10.875 | 27.875 | 47 | 24 | 28 | [5 empty] | 28 | 28 | 12.5625 | 5 | 18.9375 | 30.25 |  | 6" | 12 | 1.375 | 10.5 | R-46 | 0.125
8" | 8.625 | 8.8125 | 19 | 5 | 7 | 6 | 4 | 20.8125 | 15.8125 | 13.8125 | 32.875 | 55 | 27 | 32.875 | [5 empty] | 33.125 | 33.125 | 14.5 | 3.6875 | 18.9375 | 30.25 |  | 8" | 12 | 1.625 | 12 | R-50 | 0.15625
10" | 10.75 | 10.4375 | 23 | 6.25 | 8.5 | 7 | 5 | 25.4375 | 18.9375 | 16.6875 | [9 empty] | 39.375 | 39.375 | 18.875 | 4.875 | 21.5 | 39 |  | 10" | 12 | 1.875 | 13.75 | R-54 | 0.15625
12" | 12.75 | 11.6875 | 26.5 | 7.5 | 10 | 8 | 6 | 29.6875 | 21.6875 | 19.1875 | [9 empty] | 45.125 | 45.125 | 21.6875 | 4.875 | 21.5 | 39 |  | 12" | 16 | 2 | 15.5 | R-58 | 0.1875
14" | 14 | 12.375 | 29.5 | 8.75 | 11 | 13 | 6.5 | 33.375 | 23.375 | 21.125 | [9 empty] | 50.25 | 50.25 | 23.75 | 9.75 | 29 | 39 |  | 14" | 16 | 2.25 | 17 | R-63 | 0.21875
16" | 16 | 12.9375 | 32.5 | 10 | 12 | 14 | 7 | 36.9375 | 24.9375 | 22.9375 | [9 empty] | 55.375 | 55.375 | 25.75 | 9.75 | 29 | 30.25 |  | 16" | 16 | 2.5 | 18.5 | R-67 | 0.3125
18" | 18 | A: 13.5625; B: 36; C: 11.25; D: 13.5; E: 15; F: 8; G: 40.5625; H: 27.0625; J: 24.8125; FULL PORT T: 61.375; VALVE TO HW (FB) V: 30.5; HW OFFSET (FB) W: 5.75; HW PROJ (FB) X: 31.375; HW OD (FB) Y: 30.25 | 18" | 16 | 2.75 | 20.5 | R-71 | 0.3125
20" | 20 | 14.6875 | 38.75 | 12.5 | 15 | 20 | 9 | 44.6875 | 29.6875 | 27.1875 | [9 empty] | 66.375 | 66.375 | 31.25 | 5.75 | 31.375 | 30.25 |  | 20" | 16 | 3 | 22.5 | R-75 | 0.375
24" | 24 | 16.8125 | 46 | 15 | 17 | 20 | 10.5 | 52.8125 | 33.8125 | 31.8125 | [9 empty] | 77.625 | 77.625 | 37.875 | 16 | 37.25 | 30.25 |  | 24" | 16 | 3.5 | 25.75 | R-79 | 0.4375
(1) |  | C: CALC. BOX
(2) Crane Duo-Chek II
(3) TK Ball Valves
(4) Length does not include crowns

## Screwed Fittings
SCREWED FITTINGS
3000#
SIZE | A | B | C | D | E | F | G | H * | J * | K *
0.5 | 1.3125 | 1.5 | 1 | 2.125 | 2.1875 | 1.875 | 1.125 | 0.5 | 0.5 | 0.5
0.75 | 1.5 | 1.8125 | 1.125 | 2.3125 | 2.5625 | 2 | 1.375 | 0.5625 | 0.5625 | 0.5625
1 | 1.75 | 2.1875 | 1.3125 | 2.5 | 2.9375 | 2.375 | 1.75 | 0.6875 | 0.6875 | 0.6875
1.5 | 2.375 | 3 | 1.6875 | 3.125 | 3.6875 | 3.125 | 2.5 | 0.6875 | 0.6875 | 0.6875
2 | 2.5 | 3.3125 | 1.75 | 3.5 | 4.5625 | 3.375 | 3 | 0.75 | 0.75 | 0.75
2.5 | 3.25 | 4 | 2.0625 | 4.625 | 5.25 | 3.625 | 3.625 | 0.9375 | 0.9375 | 0.9375
6000#
SIZE | A | B | C | D | E | F | G | H * | J * | K *
0.5 | 1.5 | 1.8125 | 1.125 | 2.875 | 2.8125 | 1.875 | 1.5 | 0.5 | 0.5 | 0.5
0.75 | 1.75 | 2.1875 | 1.3125 | 3.375 | 3.125 | 2 | 1.75 | 0.5625 | 0.5625 | 0.5625
1 | 2 | 2.4375 | 1.375 | 3.625 | 3.8125 | 2.375 | 2.25 | 0.6875 | 0.6875 | 0.6875
1.5 | 2.5 | 3.3125 | 1.75 | 4.1875 | 4.75 | 3.125 | 3 | 0.6875 | 0.6875 | 0.6875
2 | 3.25 | 4 | 2.0625 | 4.625 | 5.25 | 3.375 | 3.625 | 0.75 | 0.75 | 0.75
2.5 | 3.75 | 4.75 | 2.5 | - | - | 3.625 | 4.25 | 0.9375 | 0.9375 | 0.9375
* | Thread engagement typical for H, J & K

## Weld-o-Lets
WELDOLET
CENTER OF RUN TO FACE OF FITTING
RUN SIZE | WT. OR SCH. | OUTLET SIZE
|  | 0.5 | 0.75 | 1 | 1.5 | 2 | 2.5 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24
0.5 | STD | 1.1875
| XS | 1.1875
| 160&XXS | 1.5
0.75 | STD | 1.25 | 1.4375
| XS | 1.25 | 1.4375
| 160&XXS | 1.625 | 1.75
1 | STD | 1.375 | 1.5 | 1.6875
| XS | 1.375 | 1.5 | 1.6875
| 160&XXS | 1.75 | 1.875 | 2.125
1.5 | STD | 1.6875 | 1.8125 | 2 | 2.25
| XS | 1.6875 | 1.8125 | 2 | 2.25
| 160&XXS | 2.0625 | 2.1875 | 2.4375 | 2.9375
2 | STD | 1.9375 | 2.0625 | 2.25 | 2.5 | 3.8333
| XS | 1.9375 | 2.0625 | 2.25 | 2.5 | 2.6875
| 160&XXS | 2.3125 | 2.4375 | 2.6875 | 3.1875 | 3.375
2.5 | STD | 2.1875 | 2.3125 | 2.5 | 2.75 | 2.9375 | 3.0625
| XS | 2.1875 | 2.3125 | 2.5 | 2.75 | 2.9375 | 3.0625
| 160&XXS | 2.5625 | 2.6875 | 2.9375 | 3.4375 | 3.625 | 3.875
3 | STD | 2.5 | 2.625 | 2.8125 | 3.0625 | 3.25 | 3.375 | 3.5
| XS | 2.5 | 2.625 | 2.8125 | 3.0625 | 3.25 | 3.375 | 3.5
| 160&XXS | 2.875 | 3 | 3.25 | 3.75 | 3.9375 | 4.1875 | 4.625
4 | STD | 3 | 3.125 | 3.3125 | 3.5625 | 3.75 | 3.875 | 4 | 4.25
| XS | 3 | 3.125 | 3.3125 | 3.5625 | 3.75 | 3.875 | 4 | 4.25
| 160&XXS | 3.375 | 3.5 | 3.75 | 4.25 | 4.4375 | 4.6875 | 5.125 | 5.5625
6 | STD | 4.0625 | 4.1875 | 4.375 | 4.625 | 4.8125 | 4.9375 | 5.0625 | 5.3125 | 5.6875
| XS | 4.0625 | 4.1875 | 4.375 | 4.625 | 4.8125 | 4.9375 | 5.0625 | 5.3125 | 6.375
| 160&XXS | 4.4375 | 4.5625 | 4.8125 | 5.3125 | 5.5 | 5.75 | 6.1875 | 6.625 | 7.4375
8 | STD | 5.0625 | 5.1875 | 5.375 | 5.625 | 5.8125 | 5.9375 | 6.0625 | 6.3125 | 6.6875 | 7.0625
| XS | 5.0625 | 5.1875 | 5.375 | 5.625 | 5.8125 | 5.9375 | 6.0625 | 6.3125 | 7.375 | 8.1875
| 160&XXS |  |  |  |  | 6.5 | 6.75 | 7.1875 | 7.625 | 8.4375 | *
10 | STD | 6.125 | 6.25 | 6.4375 | 6.6875 | 6.875 | 7 | 7.125 | 7.375 | 7.75 | 8.125 | 8.4375
| XS | 6.125 | 6.25 | 6.4375 | 6.6875 | 6.875 | 7 | 7.125 | 7.375 | 8.4375 | 9.25 | 9.125
| 160&XXS |  |  |  |  | 7.5625 | 7.8125 | 8.25 | 8.6875 | 9.5 | * | *
12 | STD | 7.125 | 7.25 | 7.4375 | 7.6875 | 7.875 | 8 | 8.125 | 8.375 | 8.75 | 9.125 | 9.4375 | 9.75
| XS | 7.125 | 7.25 | 7.4375 | 7.6875 | 7.875 | 8 | 8.125 | 8.375 | 9.4375 | 10.25 | 10.0625 | 10.3125
| 160&XXS |  |  |  |  | 8.5625 | 8.8125 | 9.25 | 9.6875 | 10.5 | * | * | *
14 | STD | 7.75 | 7.875 | 8.0625 | 8.3125 | 8.5 | 8.625 | 8.75 | 9 | 9.375 | 9.75 | 10.0625 | 10.375 | 10.5
| XS | 7.75 | 7.875 | 8.0625 | 8.3125 | 8.5 | 8.625 | 8.75 | 9 | 10.0625 | 10.875 | 10.6875 | 11.0625 | 11.125
| 160&XXS |  |  |  |  | 9.1875 | 9.4375 | 9.875 | 10.3125 | 11.125 | * | * | * | *
16 | STD | 8.75 | 8.875 | 9.0625 | 9.3125 | 9.5 | 9.625 | 9.75 | 10 | 10.375 | 10.75 | 11.0625 | 11.375 | 11.5 | 11.6875
| XS | 8.75 | 8.875 | 9.0625 | 9.3125 | 9.5 | 9.625 | 9.75 | 10 | 11.0625 | 11.875 | 11.6875 | 12.0625 | 11.9375 | 12.4375
| 160&XXS |  |  |  |  | 10.1875 | 10.4375 | 10.875 | 11.3125 | 12.125 | * | * | * | * | *
18 | STD | 9.75 | 9.875 | 10.0625 | 10.3125 | 10.5 | 10.625 | 10.75 | 11 | 11.375 | 11.75 | 12.0625 | 12.375 | 12.5 | 12.6875 | 13.0625
| XS | 9.75 | 9.875 | 10.0625 | 10.3125 | 10.5 | 10.625 | 10.75 | 11 | 12.0625 | 12.875 | 12.6875 | 13.0625 | 12.9375 | 13.1875 | 13.6875
| 160&XXS |  |  |  |  | 11.1875 | 11.4375 | 11.875 | 12.3125 | 13.125 | * | * | * | * | * | *
20 | STD | 10.75 | 10.875 | 11.0625 | 11.3125 | 11.5 | 11.625 | 11.75 | 12 | 12.375 | 12.75 | 13.0625 | 13.375 | 13.5 | 13.6875 | 13.8125 | 14.625
| XS | 10.75 | 10.875 | 11.0625 | 11.3125 | 11.5 | 11.625 | 11.75 | 12 | 13.0625 | 13.875 | 13.6875 | 14.0625 | 13.9375 | 14.1875 | 14.375 | 15
| 160&XXS |  |  |  |  | 12.1875 | 12.4375 | 12.875 | 13.3125 | 14.125 | * | * | * | * | * | * | *
24 | STD | 12.75 | 12.875 | 13.0625 | 13.3125 | 13.5 | 13.625 | 13.75 | 14 | 14.375 | 14.75 | 15.0625 | 15.375 | 15.5 | 15.6875 | 15.8125 | 16 | 17.375
| XS | 12.75 | 12.875 | 13.0625 | 13.3125 | 13.5 | 13.625 | 13.75 | 14 | 15.0625 | 15.875 | 15.6875 | 16.0625 | 15.9375 | 16.1875 | 16.375 | 16.6875 | 17.5
| 160&XXS |  |  |  |  | 14.1875 | 14.4375 | 14.875 | 15.3125 | 16.125 | * | * | * | * | * | * | * | *
* | USE HEVY WALL WELDOLET

## W Shapes
2017-06-13 14:31 | [10 empty] | Password
[6 empty] | Flg. Width "bf" |  |  |  |  | ABB
|  | W Shapes |  |  |  | Flg Gage
k1
|  |  | Flg. Thk "tf" | [5 empty] | k
Web Gage
Depth
"d"
Web thk. "tw"
Shapes in shaded rows are not available from domestic producers
Beam | Depth | Web Thk. | Flg. Width | Flg. Thk. | k | k1 | Flange | Web | Sq. Ft.- Surf | Sq.M.- Surf | Weight
Size | d | tw | bf | tf |  |  | Bolt Gage | Bolt Gage | Area - per Ft | Area - per M | Kg per M
W44x285 | 44 | 1 | 11.75 | 1.75 | 2.6875 | 1.375 |  |  | 11.0833 | 3.3782 | 424.1268 | 285
W44X248 | 43.625 | 0.875 | 11.75 | 1.5625 | 2.5 | 1.3125 |  |  | 11.0417 | 3.3655 | 369.0647 | 248
W44x224 | 43.25 | 0.8125 | 11.75 | 1.4375 | 2.3125 | 1.3125 |  |  | 10.9896 | 3.3496 | 333.3487 | 224
W44x198 | 42.875 | 0.6875 | 11.75 | 1.25 | 2.125 | 1.25 |  |  | 10.9479 | 3.3369 | 294.6565 | 198
W40x328 | 40 | 0.9375 | 17.875 | 1.75 | 3.125 | 1.6875 |  |  | 12.4688 | 3.8005 | 488.1178 | 328
W40x298 | 39.75 | 0.8125 | 17.875 | 1.5625 | 3 | 1.625 |  |  | 12.4479 | 3.7941 | 443.4729 | 298
W40x268 | 39.375 | 0.75 | 17.75 | 1.4375 | 2.8125 | 1.5625 |  |  | 12.3542 | 3.7656 | 398.828 | 268
W40x244 | 39 | 0.6875 | 17.75 | 1.25 | 2.625 | 1.5625 |  |  | 12.3021 | 3.7497 | 363.112 | 244
W40x221 | 38.625 | 0.6875 | 17.75 | 1.0625 | 2.4375 | 1.5625 |  |  | 12.2396 | 3.7306 | 328.8843 | 221
W40x192 | 38.25 | 0.6875 | 17.75 | 0.8125 | 2.25 | 1.5625 |  |  | 12.1771 | 3.7116 | 285.7275 | 192
W40x655 | 43.625 | 2 | 16.875 | 3.5625 | 4.9375 | 2.25 |  |  | 12.5625 | 3.8291 | 974.7474 | 655
W40x593 | 43 | 1.8125 | 16.75 | 3.25 | 4.625 | 2.125 |  |  | 12.4479 | 3.7941 | 882.4813 | 593
W40x531 | 42.375 | 1.625 | 16.5 | 2.9375 | 4.3125 | 2 |  |  | 12.2917 | 3.7465 | 790.2151 | 531
W40x480 | 41.75 | 1.4375 | 16.375 | 2.625 | 4 | 2 |  |  | 12.1771 | 3.7116 | 714.3187 | 480
W40x436 | 41.375 | 1.3125 | 16.25 | 2.375 | 3.8125 | 1.9375 |  |  | 12.0938 | 3.6862 | 648.8395 | 436
W40x397 | 41 | 1.25 | 16.125 | 2.1875 | 3.625 | 1.875 |  |  | 12 | 3.6576 | 590.8011 | 397
W40x362 | 40.5 | 1.125 | 16 | 2 | 3.375 | 1.8125 |  |  | 11.8958 | 3.6259 | 538.7154 | 362
W40x324 | 40.125 | 1 | 15.875 | 1.8125 | 3.1875 | 1.75 |  |  | 11.8125 | 3.6005 | 482.1652 | 324
W40x297 | 39.875 | 0.9375 | 15.875 | 1.625 | 3.0625 | 1.6875 |  |  | 11.7812 | 3.5909 | 441.9847 | 297
W40x277 | 39.75 | 0.8125 | 15.875 | 1.5625 | 3 | 1.625 |  |  | 11.7812 | 3.5909 | 412.2214 | 277
W40x249 | 39.375 | 0.75 | 15.75 | 1.4375 | 2.8125 | 1.5625 |  |  | 11.6875 | 3.5624 | 370.5528 | 249
W40x215 | 39 | 0.625 | 15.75 | 1.25 | 2.625 | 1.5625 |  |  | 11.6458 | 3.5497 | 319.9553 | 215
W40x199 | 38.625 | 0.625 | 15.75 | 1.0625 | 2.4375 | 1.5625 |  |  | 11.5833 | 3.5306 | 296.1446 | 199
W40x183 | 39 | 0.625 | 11.75 | 1.25 | 2.625 | 1.5625 |  |  | 10.3125 | 3.1433 | 272.334 | 183
W40x167 | 38.625 | 0.625 | 11.75 | 1 | 2.4375 | 1.5625 |  |  | 10.25 | 3.1242 | 248.5234 | 167
W40x149 | 38.25 | 0.625 | 11.75 | 0.8125 | 2.25 | 1.5 |  |  | 10.1875 | 3.1052 | 221.7364 | 149
W36x848 | 42.5 | 2.5 | 18.125 | 4.5 | 5.6875 | 2.25 |  |  | 12.7083 | 3.8735 | 1261.9631 | 848
W36x798 | 42 | 2.375 | 18 | 4.3125 | 5.4375 | 2.1875 |  |  | 12.6042 | 3.8418 | 1187.5549 | 798
W36x720 | 41.25 | 2.1875 | 17.75 | 3.875 | 5.0625 | 2.0625 |  |  | 12.4271 | 3.7878 | 1071.4781 | 720
W36x650 | 40.5 | 2 | 17.625 | 3.5625 | 4.6875 | 2 |  |  | 12.2917 | 3.7465 | 967.3066 | 650
W36x588 | 39.875 | 1.8125 | 17.375 | 3.25 | 4.375 | 1.875 |  |  | 12.1354 | 3.6989 | 875.0405 | 588
W36x527 | 39.25 | 1.625 | 17.25 | 2.9375 | 4.0625 | 1.75 |  |  | 12.0208 | 3.664 | 784.2625 | 527
W36x485 | 38.75 | 1.5 | 17.125 | 2.6875 | 3.8125 | 1.75 |  |  | 11.9167 | 3.6322 | 721.7596 | 485
W36x439 | 38.25 | 1.375 | 17 | 2.4375 | 3.5625 | 1.625 |  |  | 11.8125 | 3.6005 | 653.304 | 439
W36x393 | 37.75 | 1.25 | 16.875 | 2.1875 | 3.3125 | 1.625 |  |  | 11.7083 | 3.5687 | 584.8485 | 393
W36x359 | 37.375 | 1.125 | 16.75 | 2 | 3.125 | 1.5625 |  |  | 11.625 | 3.5433 | 534.2509 | 359
W36x328 | 37.125 | 1 | 16.625 | 1.875 | 3 | 1.5 |  |  | 11.5625 | 3.5243 | 488.1178 | 328
W36x300 | 36.75 | 0.9375 | 16.625 | 1.6875 | 2.8125 | 1.5 | 5.5 | 3.75 | 11.5104 | 3.5084 | 446.4492 | 300
W36x280 | 36.5 | 0.875 | 16.625 | 1.5625 | 2.6875 | 1.5 | 5.5 | 3.75 | 11.4792 | 3.4989 | 416.6859 | 280
W36x260 | 36.25 | 0.812 | 16.5 | 1.4375 | 2.5625 | 1.5 | 5.5 | 3.5 | 11.4063 | 3.4767 | 386.9227 | 260
W36x245 | 36.125 | 0.8125 | 16.5 | 1.375 | 2.5 | 1.4375 | 5.5 | 3.5 | 11.3854 | 3.4703 | 364.6002 | 245
W36x230 | 35.875 | 0.75 | 16.5 | 1.25 | 2.375 | 1.4375 | 5.5 | 3.5 | 11.3542 | 3.4608 | 342.2777 | 230
W36x256 | 37.375 | 1 | 12.25 | 1.75 | 2.625 | 1.3125 | 5.5 |  | 10.1458 | 3.0925 | 380.97 | 256
W36x232 | 37.125 | 0.875 | 12.125 | 1.5625 | 2.5 | 1.25 | 5.5 |  | 10.0833 | 3.0734 | 345.2541 | 232
W36x210 | 36.75 | 0.8125 | 12.125 | 1.375 | 2.3125 | 1.25 | 5.5 | 3.5 | 10.0312 | 3.0575 | 312.5144 | 210
W36x194 | 36.5 | 0.75 | 12.125 | 1.25 | 2.1875 | 1.1875 | 5.5 | 3.5 | 10 | 3.048 | 288.7038 | 194
W36x182 | 36.375 | 0.75 | 12.125 | 1.1875 | 2.125 | 1.1875 | 5.5 | 3.25 | 9.9792 | 3.0417 | 270.8459 | 182
W36x170 | 36.125 | 0.6875 | 12 | 1.125 | 2 | 1.1875 | 5.5 | 3.25 | 9.9062 | 3.0194 | 252.9879 | 170
W36x160 | 36 | 0.625 | 12 | 1 | 1.9375 | 1.125 | 5.5 | 3.25 | 9.8958 | 3.0163 | 238.1062 | 160
W36x150 | 35.875 | 0.625 | 12 | 0.9375 | 1.875 | 1.125 | 5.5 | 3 | 9.875 | 3.0099 | 223.2246 | 150
W36x135 | 35.5 | 0.625 | 12 | 0.8125 | 1.6875 | 1.125 | 5.5 | 3 | 9.8125 | 2.9909 | 200.9021 | 135
W33x619 | 38.5 | 2 | 16.875 | 3.5625 | 4.375 | 1.75 |  |  | 11.7083 | 3.5687 | 921.1735 | 619
W33x567 | 37.875 | 1.8125 | 16.75 | 3.25 | 4.0625 | 1.6875 |  |  | 11.5938 | 3.5338 | 843.789 | 567
W33x515 | 37.375 | 1.625 | 16.625 | 3 | 3.812 | 1.625 |  |  | 11.5 | 3.5052 | 766.4045 | 515
W33x468 | 36.75 | 1.5 | 16.5 | 2.75 | 3.5 | 1.5625 |  |  | 11.375 | 3.4671 | 696.4608 | 468
W33x424 | 36.375 | 1.375 | 16.375 | 2.5 | 3.3125 | 1.4375 |  |  | 11.2917 | 3.4417 | 630.9816 | 424
W33x387 | 36 | 1.25 | 16.25 | 2.25 | 3.125 | 1.375 |  |  | 11.2083 | 3.4163 | 575.9195 | 387
W33x354 | 35.5 | 1.1875 | 16.125 | 2.0625 | 2.875 | 1.375 |  |  | 11.0938 | 3.3814 | 526.8101 | 354
W33x318 | 35.125 | 1.0625 | 16 | 1.875 | 2.6875 | 1.3125 |  |  | 11.0104 | 3.356 | 473.2362 | 318
W33x291 | 34.875 | 1 | 15.875 | 1.75 | 2.5625 | 1.25 |  |  | 10.9375 | 3.3338 | 433.0557 | 291
W33x263 | 34.5 | 0.875 | 15.75 | 1.5625 | 2.375 | 1.1875 |  |  | 10.8542 | 3.3084 | 391.3871 | 263
W33x241 | 34.125 | 0.8125 | 15.875 | 1.375 | 2.1875 | 1.1875 | 5.5 | 3.5 | 10.8438 | 3.3052 | 358.6475 | 241
W33x221 | 33.875 | 0.75 | 15.75 | 1.25 | 2.0625 | 1.1875 | 5.5 | 3.5 | 10.7708 | 3.283 | 328.8843 | 221
W33x201 | 33.625 | 0.6875 | 15.75 | 1.125 | 1.9375 | 1.125 | 5.5 | 3.25 | 10.7396 | 3.2734 | 299.121 | 201
W33x169 | 33.875 | 0.6875 | 11.5 | 1.25 | 2.0625 | 1.125 |  |  | 9.3646 | 2.8543 | 251.4997 | 169
W33x152 | 33.5 | 0.625 | 11.625 | 1.0625 | 1.875 | 1.125 | 5.5 | 3.25 | 9.3542 | 2.8512 | 226.2009 | 152
W33x141 | 33.25 | 0.625 | 11.5 | 0.9375 | 1.75 | 1.0625 | 5.5 | 3 | 9.2708 | 2.8258 | 209.8311 | 141
W33x130 | 33.125 | 0.5625 | 11.5 | 0.875 | 1.6875 | 1.0625 | 5.5 | 3 | 9.2604 | 2.8226 | 193.4613 | 130
W33x118 | 32.875 | 0.5625 | 11.5 | 0.75 | 1.5625 | 1.0625 | 5.5 | 2.75 | 9.2188 | 2.8099 | 175.6034 | 118
W30x581 | 35.375 | 2 | 16.25 | 3.5625 | 4.3125 | 1.6875 |  |  | 10.9792 | 3.3465 | 864.6233 | 581
W30x526 | 34.75 | 1.8125 | 16 | 3.25 | 4 | 1.625 |  |  | 10.8229 | 3.2988 | 782.7743 | 526
W30x477 | 34.25 | 1.625 | 15.875 | 3 | 3.75 | 1.5625 |  |  | 10.7292 | 3.2703 | 709.8542 | 477
W30x433 | 33.625 | 1.5 | 15.75 | 2.6875 | 3.4375 | 1.5 |  |  | 10.6042 | 3.2322 | 644.375 | 433
W30x391 | 33.25 | 1.375 | 15.625 | 2.4375 | 3.25 | 1.4375 |  |  | 10.5208 | 3.2068 | 581.8721 | 391
W30x357 | 32.75 | 1.25 | 15.5 | 2.25 | 3 | 1.375 |  |  | 10.4167 | 3.175 | 531.2746 | 357
W30x326 | 32.375 | 1.125 | 15.375 | 2.0625 | 2.8125 | 1.3125 |  |  | 10.3333 | 3.1496 | 485.1415 | 326
W30x292 | 32 | 1 | 15.25 | 1.875 | 2.625 | 1.25 |  |  | 10.25 | 3.1242 | 434.5439 | 292
W30x261 | 31.625 | 0.9375 | 15.125 | 1.625 | 2.4375 | 1.1875 |  |  | 10.1562 | 3.0956 | 388.4108 | 261
W30x235 | 31.25 | 0.8125 | 15 | 1.5 | 2.25 | 1.125 |  |  | 10.0729 | 3.0702 | 349.7186 | 235
W30x211 | 31 | 0.75 | 15.125 | 1.3125 | 2.125 | 1.125 | 5.5 | 3.5 | 10.0833 | 3.0734 | 314.0026 | 211
W30x191 | 30.625 | 0.6875 | 15 | 1.1875 | 1.9375 | 1.0625 | 5.5 | 3.25 | 9.9896 | 3.0448 | 284.2393 | 191
W30x173 | 30.5 | 0.625 | 15 | 1.0625 | 1.875 | 1.0625 | 5.5 | 3.25 | 9.9792 | 3.0417 | 257.4524 | 173
W30x148 | 30.625 | 0.625 | 10.5 | 1.1875 | 2 | 1 |  |  | 8.5 | 2.5908 | 220.2483 | 148
W30x132 | 30.25 | 0.625 | 10.5 | 1 | 1.75 | 1.0625 | 5.5 | 3 | 8.4375 | 2.5718 | 196.4377 | 132
W30x124 | 30.125 | 0.5625 | 10.5 | 0.9375 | 1.6875 | 1 | 5.5 | 3 | 8.4271 | 2.5686 | 184.5323 | 124
W30x116 | 30 | 0.5625 | 10.5 | 0.875 | 1.625 | 1 | 5.5 | 3 | 8.4062 | 2.5622 | 172.627 | 116
W30x108 | 29.875 | 0.5625 | 10.5 | 0.75 | 1.5625 | 1 | 5.5 | 3 | 8.3854 | 2.5559 | 160.7217 | 108
W30x99 | 29.625 | 0.5 | 10.5 | 0.6875 | 1.4375 | 1 | 5.5 | 2.75 | 8.3542 | 2.5464 | 147.3282 | 99
W30x90 | 29.5 | 0.5 | 10.375 | 0.5625 | 1.3125 | 1 |  |  | 8.2917 | 2.5273 | 133.9348 | 90
W27x539 | 32.5 | 2 | 15.25 | 3.5625 | 4.25 | 1.625 |  |  | 10.1667 | 3.0988 | 802.1204 | 539
W27x494 | 32 | 1.8125 | 15.125 | 3.25 | 4 | 1.5625 |  |  | 10.0729 | 3.0702 | 735.153 | 494
W27x448 | 31.375 | 1.625 | 15 | 3 | 3.6875 | 1.5 |  |  | 9.9583 | 3.0353 | 666.6975 | 448
W27x407 | 30.875 | 1.5 | 14.75 | 2.75 | 3.4375 | 1.4375 |  |  | 9.8125 | 2.9909 | 605.6828 | 407
W27x368 | 30.375 | 1.375 | 14.625 | 2.5 | 3.1875 | 1.3125 |  |  | 9.7083 | 2.9591 | 547.6444 | 368
W27x336 | 30 | 1.25 | 14.5 | 2.25 | 3 | 1.3125 |  |  | 9.625 | 2.9337 | 500.0231 | 336
W27x307 | 29.625 | 1.1875 | 14.5 | 2.0625 | 2.8125 | 1.25 |  |  | 9.5729 | 2.9178 | 575.9195 | 387
W27x281 | 29.25 | 1.0625 | 14.375 | 1.9375 | 2.625 | 1.1875 |  |  | 9.4896 | 2.8924 | 418.1741 | 281
W27x258 | 29 | 1 | 14.25 | 1.75 | 2.5 | 1.125 |  |  | 9.4167 | 2.8702 | 383.9463 | 258
W27x235 | 28.625 | 0.9375 | 14.25 | 1.625 | 2.3125 | 1.125 |  |  | 9.3646 | 2.8543 | 349.7186 | 235
W27x217 | 28.375 | 0.8125 | 14.125 | 1.5 | 2.1875 | 1.0625 |  |  | 9.3021 | 2.8353 | 322.9316 | 217
W27x194 | 28.125 | 0.75 | 14 | 1.3125 | 2.0625 | 1 |  |  | 9.2292 | 2.8131 | 288.7038 | 194
W27x178 | 27.75 | 0.75 | 14.125 | 1.1875 | 1.875 | 1.0625 | 5.5 | 3.25 | 9.2083 | 2.8067 | 264.8932 | 178
W27x161 | 27.625 | 0.6875 | 14 | 1.0625 | 1.8125 | 1 | 5.5 | 3.25 | 9.1562 | 2.7908 | 239.5944 | 161
W27x146 | 27.375 | 0.625 | 14 | 1 | 1.6875 | 1 | 5.5 | 3 | 9.125 | 2.7813 | 217.272 | 146
W27x129 | 27.625 | 0.625 | 10 | 1.125 | 1.8125 | 0.9375 | 5.5 |  | 7.8333 | 2.3876 | 191.9732 | 129
W27x114 | 27.25 | 0.5625 | 10.125 | 0.9375 | 1.625 | 0.9375 | 5.5 | 3 | 7.8229 | 2.3844 | 169.6507 | 114
W27x102 | 27.125 | 0.5 | 10 | 0.8125 | 1.5625 | 0.9375 | 5.5 | 3 | 7.7708 | 2.3686 | 151.7927 | 102
W27x94 | 26.875 | 0.5 | 10 | 0.75 | 1.4375 | 0.9375 | 5.5 | 2.75 | 7.7292 | 2.3559 | 139.8874 | 94
W27x84 | 26.75 | 0.4375 | 10 | 0.625 | 1.375 | 0.9375 | 5.5 | 2.75 | 7.7188 | 2.3527 | 125.0058 | 84
W24x492 | 29.625 | 2 | 14.125 | 3.5625 | 4.3125 | 1.5625 |  |  | 9.3125 | 2.8385 | 732.1767 | 492
W24x450 | 29.125 | 1.8125 | 14 | 3.25 | 4.0625 | 1.5 |  |  | 9.2188 | 2.8099 | 669.6738 | 450
W24x408 | 28.5 | 1.625 | 13.75 | 3 | 3.75 | 1.375 |  |  | 9.0625 | 2.7623 | 607.1709 | 408
W24x370 | 28 | 1.5 | 13.625 | 2.75 | 3.5 | 1.3125 |  |  | 8.9583 | 2.7305 | 550.6207 | 370
W24x335 | 27.5 | 1.375 | 13.5 | 2.5 | 3.25 | 1.25 |  |  | 8.8542 | 2.6988 | 498.535 | 335
W24x306 | 27.125 | 1.25 | 13.375 | 2.25 | 3.0625 | 1.1875 |  |  | 8.7708 | 2.6734 | 455.3782 | 306
W24x279 | 26.75 | 1.1875 | 13.25 | 2.0625 | 2.875 | 1.125 |  |  | 8.6771 | 2.6448 | 415.1978 | 279
W24x250 | 26.375 | 1.0625 | 13.125 | 1.875 | 2.6875 | 1.125 |  |  | 8.5938 | 2.6194 | 372.041 | 250
W24x229 | 26 | 1 | 13.125 | 1.75 | 2.5 | 1 |  |  | 8.5417 | 2.6035 | 340.7896 | 229
W24x207 | 25.75 | 0.875 | 13 | 1.5625 | 2.375 | 1 |  |  | 8.4792 | 2.5845 | 308.05 | 207
W24x192 | 25.5 | 0.8125 | 13 | 1.4375 | 2.25 | 1 |  |  | 8.4479 | 2.5749 | 285.7275 | 192
W24x176 | 25.25 | 0.75 | 12.875 | 1.3125 | 2.125 | 0.9375 |  |  | 8.375 | 2.5527 | 261.9169 | 176
W24x162 | 25 | 0.6875 | 13 | 1.25 | 2 | 1.0625 | 5.5 | 3.25 | 8.3854 | 2.5559 | 241.0826 | 162
W24x146 | 24.75 | 0.625 | 12.875 | 1.0625 | 1.875 | 1.0625 | 5.5 | 3.25 | 8.3125 | 2.5337 | 217.272 | 146
W24x131 | 24.5 | 0.625 | 12.875 | 0.9375 | 1.75 | 1.0625 | 5.5 | 3 | 8.2708 | 2.521 | 194.9495 | 131
W24x117 | 24.25 | 0.5625 | 12.75 | 0.875 | 1.625 | 1 | 5.5 | 3 | 8.1979 | 2.4987 | 174.1152 | 117
W24x104 | 24 | 0.5 | 12.75 | 0.75 | 1.5 | 1 | 5.5 | 2.75 | 8.1667 | 2.4892 | 154.7691 | 104
W24x103 | 24.5 | 0.5625 | 9 | 1 | 1.75 | 0.8125 | 5.5 |  | 6.9896 | 2.1304 | 153.2809 | 103
W24x94 | 24.25 | 0.5 | 9.125 | 0.875 | 1.625 | 1 | 5.5 | 3 | 7 | 2.1336 | 139.8874 | 94
W24x84 | 24.125 | 0.5 | 9 | 0.75 | 1.5625 | 0.9375 | 5.5 | 3 | 6.9375 | 2.1146 | 125.0058 | 84
W24x76 | 23.875 | 0.4375 | 9 | 0.6875 | 1.4375 | 0.9375 | 5.5 | 2.75 | 6.9062 | 2.105 | 113.1005 | 76
W24x68 | 23.75 | 0.4375 | 9 | 0.5625 | 1.375 | 0.9375 | 5.5 | 2.75 | 6.8854 | 2.0987 | 101.1952 | 68
W24x62 | 23.75 | 0.4375 | 7 | 0.5625 | 1.375 | 0.9375 | 3.5 | 2.75 | 6.2188 | 1.8955 | 92.2662 | 62
W24x55 | 23.625 | 0.375 | 7 | 0.5 | 1.3125 | 0.9375 | 3.5 | 2.75 | 6.2083 | 1.8923 | 81.849 | 55
W21x402 | 26 | 1.75 | 13.375 | 3.125 | 3.875 | 1.4375 |  |  | 8.5 | 2.5908 | 598.2419 | 402
W21x364 | 25.5 | 1.5625 | 13.25 | 2.875 | 3.625 | 1.375 |  |  | 8.4062 | 2.5622 | 541.6917 | 364
W21x333 | 25 | 1.4375 | 13.125 | 2.625 | 3.375 | 1.3125 |  |  | 8.3021 | 2.5305 | 495.5586 | 333
W21x300 | 24.5 | 1.3125 | 13 | 2.375 | 3.125 | 1.25 |  |  | 8.1979 | 2.4987 | 446.4492 | 300
W21x275 | 24.125 | 1.25 | 12.875 | 2.1875 | 3 | 1.1875 |  |  | 8.1042 | 2.4702 | 409.2451 | 275
W21x248 | 23.75 | 1.125 | 12.75 | 2 | 2.75 | 1.125 |  |  | 8.0208 | 2.4448 | 369.0647 | 248
W21x223 | 23.375 | 1 | 12.625 | 1.8125 | 2.5625 | 1.0625 |  |  | 7.9375 | 2.4194 | 331.8606 | 223
W21x201 | 23 | 0.9375 | 12.625 | 1.625 | 2.375 | 1 |  |  | 7.8854 | 2.4035 | 299.121 | 201
W21x182 | 22.75 | 0.8125 | 12.5 | 1.5 | 2.25 | 1 |  |  | 7.8229 | 2.3844 | 270.8459 | 182
W21x166 | 22.5 | 0.75 | 12.375 | 1.375 | 2.125 | 0.9375 |  |  | 7.75 | 2.3622 | 247.0352 | 166
W21x147 | 22 | 0.75 | 12.5 | 1.125 | 1.875 | 1.0625 | 5.5 | 3.25 | 7.7083 | 2.3495 | 218.7601 | 147
W21x132 | 21.875 | 0.625 | 12.5 | 1.0625 | 1.8125 | 1 | 5.5 | 3 | 7.7083 | 2.3495 | 196.4377 | 132
W21x122 | 21.625 | 0.625 | 12.375 | 0.9375 | 1.6875 | 1 | 5.5 | 3 | 7.625 | 2.3241 | 181.556 | 122
W21x111 | 21.5 | 0.5625 | 12.375 | 0.875 | 1.625 | 0.9375 | 5.5 | 2.75 | 7.6146 | 2.3209 | 165.1862 | 111
W21x101 | 21.375 | 0.5 | 12.25 | 0.8125 | 1.5625 | 0.9375 | 5.5 | 2.75 | 7.5625 | 2.3051 | 150.3046 | 101
W21x93 | 21.625 | 0.5625 | 8.375 | 0.9375 | 1.6875 | 1 | 5.5 | 3 | 6.3021 | 1.9209 | 138.3993 | 93
W21x83 | 21.375 | 0.5 | 8.375 | 0.8125 | 1.5625 | 0.9375 | 5.5 | 2.75 | 6.2708 | 1.9114 | 123.5176 | 83
W21x73 | 21.25 | 0.4375 | 8.25 | 0.75 | 1.5 | 0.9375 | 5.5 | 2.75 | 6.2188 | 1.8955 | 108.636 | 73
W21x68 | 21.125 | 0.4375 | 8.25 | 0.6875 | 1.4375 | 0.875 | 5.5 | 2.75 | 6.1979 | 1.8891 | 101.1952 | 68
W21x62 | 21 | 0.375 | 8.25 | 0.625 | 1.375 | 0.875 | 5.5 | 2.5 | 6.1875 | 1.886 | 92.2662 | 62
W21x57 | 21 | 0.375 | 6.5 | 0.625 | 1.375 | 0.875 | 3.5 | 2.75 | 5.6042 | 1.7082 | 84.8254 | 57
W21x50 | 20.875 | 0.375 | 6.5 | 0.5625 | 1.3125 | 0.875 | 3.5 | 2.5 | 5.5833 | 1.7018 | 74.4082 | 50
W21x44 | 20.625 | 0.375 | 6.5 | 0.4375 | 1.1875 | 0.875 | 3.5 | 2.5 | 5.5417 | 1.6891 | 65.4792 | 44
W18x311 | 22.375 | 1.5 | 12 | 2.75 | 3.4375 | 1.1875 |  |  | 7.4792 | 2.2797 | 462.819 | 311
W18x283 | 21.875 | 1.375 | 11.875 | 2.5 | 3.1875 | 1.1875 |  |  | 7.375 | 2.2479 | 421.1504 | 283
W18x258 | 21.5 | 1.25 | 11.75 | 2.3125 | 3 | 1.125 |  |  | 7.2917 | 2.2225 | 383.9463 | 258
W18x234 | 21 | 1.1875 | 11.625 | 2.125 | 2.75 | 1 |  |  | 7.1771 | 2.1876 | 348.2304 | 234
W18x211 | 20.625 | 1.0625 | 11.5 | 1.9375 | 2.5625 | 1 |  |  | 7.0938 | 2.1622 | 314.0026 | 211
W18x192 | 20.375 | 1 | 11.5 | 1.75 | 2.4375 | 0.9375 |  |  | 7.0625 | 2.1527 | 285.7275 | 192
W18x175 | 20 | 0.875 | 11.375 | 1.5625 | 2.25 | 0.875 |  |  | 6.9792 | 2.1273 | 260.4287 | 175
W18x158 | 19.75 | 0.8125 | 11.25 | 1.4375 | 2.125 | 0.875 |  |  | 6.9062 | 2.105 | 235.1299 | 158
W18x143 | 19.5 | 0.75 | 11.25 | 1.3125 | 2 | 0.8125 |  |  | 6.875 | 2.0955 | 212.8075 | 143
W18x130 | 19.25 | 0.6875 | 11.125 | 1.1875 | 1.875 | 0.8125 |  |  | 6.8021 | 2.0733 | 193.4613 | 130
W18x119 | 19 | 0.625 | 11.25 | 1.0625 | 1.75 | 0.9375 | 5.5 | 3 | 6.8125 | 2.0765 | 177.0915 | 119
W18x106 | 18.75 | 0.5625 | 11.25 | 0.9375 | 1.625 | 0.9375 | 5.5 | 3 | 6.7812 | 2.0669 | 157.7454 | 106
W18x97 | 18.625 | 0.5625 | 11.125 | 0.875 | 1.5625 | 0.875 | 5.5 | 2.75 | 6.7188 | 2.0479 | 144.3519 | 97
W18x86 | 18.375 | 0.5 | 11.125 | 0.75 | 1.4375 | 0.875 | 5.5 | 2.75 | 6.6875 | 2.0384 | 127.9821 | 86
W18x76 | 18.25 | 0.4375 | 11 | 0.6875 | 1.375 | 0.8125 | 5.5 | 2.75 | 6.6354 | 2.0225 | 113.1005 | 76
W18x71 | 18.5 | 0.5 | 7.625 | 0.8125 | 1.5 | 0.875 | 3.5 | 2.75 | 5.5417 | 1.6891 | 105.6596 | 71
W18x65 | 18.375 | 0.4375 | 7.625 | 0.75 | 1.4375 | 0.875 | 3.5 | 2.75 | 5.5312 | 1.6859 | 96.7307 | 65
W18x60 | 18.25 | 0.4375 | 7.5 | 0.6875 | 1.375 | 0.8125 | 3.5 | 2.75 | 5.4688 | 1.6669 | 89.2898 | 60
W18x55 | 18.125 | 0.375 | 7.5 | 0.625 | 1.3125 | 0.8125 | 3.5 | 2.75 | 5.4583 | 1.6637 | 81.849 | 55
W18x50 | 18 | 0.375 | 7.5 | 0.5625 | 1.25 | 0.8125 | 3.5 | 2.5 | 5.4375 | 1.6574 | 74.4082 | 50
W18x46 | 18 | 0.375 | 6 | 0.625 | 1.25 | 0.8125 | 3.5 | 2.5 | 4.9375 | 1.505 | 68.4555 | 46
W18x40 | 17.875 | 0.3125 | 6 | 0.5 | 1.1875 | 0.8125 | 3.5 | 2.5 | 4.9271 | 1.5018 | 59.5266 | 40
W18x35 | 17.75 | 0.3125 | 6 | 0.4375 | 1.125 | 0.75 | 3.5 | 2.5 | 4.9062 | 1.4954 | 52.0857 | 35
W16x100 | 17 | 0.5625 | 10.375 | 1 | 1.6875 | 0.9375 | 5.5 | 3 | 6.1979 | 1.8891 | 148.8164 | 100
W16x89 | 16.75 | 0.5 | 10.375 | 0.875 | 1.5625 | 0.875 | 5.5 | 2.75 | 6.1667 | 1.8796 | 132.4466 | 89
W16x77 | 16.5 | 0.4375 | 10.25 | 0.75 | 1.4375 | 0.875 | 5.5 | 2.75 | 6.0938 | 1.8574 | 114.5886 | 77
W16x67 | 16.375 | 0.375 | 10.25 | 0.6875 | 1.375 | 0.8125 | 5.5 | 2.75 | 6.0833 | 1.8542 | 99.707 | 67
W16x57 | 16.375 | 0.4375 | 7.125 | 0.6875 | 1.375 | 0.875 | 3.5 | 2.75 | 5.0312 | 1.5335 | 84.8254 | 57
W16x50 | 16.25 | 0.375 | 7.125 | 0.625 | 1.3125 | 0.8125 | 3.5 | 2.75 | 5.0208 | 1.5304 | 74.4082 | 50
W16x45 | 16.125 | 0.375 | 7 | 0.5625 | 1.25 | 0.8125 | 3.5 | 2.5 | 4.9583 | 1.5113 | 66.9674 | 45
W16x40 | 16 | 0.3125 | 7 | 0.5 | 1.1875 | 0.8125 | 3.5 | 2.5 | 4.9479 | 1.5081 | 59.5266 | 40
W16x36 | 15.875 | 0.3125 | 7 | 0.4375 | 1.125 | 0.75 | 3.5 | 2.5 | 4.9271 | 1.5018 | 53.5739 | 36
W16x31 | 15.875 | 0.25 | 5.5 | 0.4375 | 1.125 | 0.75 | 2.75 | 2.5 | 4.4375 | 1.3526 | 46.1331 | 31
W16x26 | 15.75 | 0.25 | 5.5 | 0.375 | 1.0625 | 0.75 | 2.75 | 2.25 | 4.4167 | 1.3462 | 38.6923 | 26
W14x730 | 22.375 | 3.0625 | 17.875 | 4.9375 | 5.5625 | 2.1875 | na | na | 9.1771 | 2.7972 | 1086.3598 | 730
W14x665 | 21.625 | 2.8125 | 17.625 | 4.5 | 5.1875 | 2.0625 | na | na | 9.0104 | 2.7464 | 989.6291 | 665
W14x605 | 20.875 | 2.625 | 17.375 | 4.1875 | 4.8125 | 1.9375 | na | na | 8.8333 | 2.6924 | 900.3392 | 605
W14x550 | 20.25 | 2.375 | 17.25 | 3.8125 | 4.5 | 1.8125 | na | na | 8.7292 | 2.6607 | 818.4902 | 550
W14x500 | 19.625 | 2.1875 | 17 | 3.5 | 4.1875 | 1.75 | na | na | 8.5729 | 2.613 | 744.082 | 500
W14x455 | 19 | 2 | 16.875 | 3.1875 | 3.875 | 1.625 | na | na | 8.4583 | 2.5781 | 677.1146 | 455
W14x426 | 18.625 | 1.875 | 16.75 | 3.0625 | 3.6875 | 1.5625 | na | na | 8.375 | 2.5527 | 633.9579 | 426
W14x398 | 18.25 | 1.75 | 16.625 | 2.875 | 3.5 | 1.5 | na | na | 8.2917 | 2.5273 | 592.2893 | 398
W14x370 | 17.875 | 1.625 | 16.5 | 2.6875 | 3.3125 | 1.4375 | na | na | 8.2083 | 2.5019 | 550.6207 | 370
W14x342 | 17.5 | 1.5625 | 16.375 | 2.5 | 3.125 | 1.375 | na | na | 8.1146 | 2.4733 | 508.9521 | 342
W14x311 | 17.125 | 1.4375 | 16.25 | 2.25 | 2.9375 | 1.3125 | na | na | 8.0312 | 2.4479 | 462.819 | 311
W14x283 | 16.75 | 1.3125 | 16.125 | 2.0625 | 2.75 | 1.25 | na | na | 7.9479 | 2.4225 | 421.1504 | 283
W14x257 | 16.375 | 1.1875 | 16 | 1.875 | 2.5625 | 1.1875 | na | na | 7.8646 | 2.3971 | 382.4582 | 257
W14x233 | 16 | 1.0625 | 15.875 | 1.75 | 2.375 | 1.1875 | na | na | 7.7812 | 2.3717 | 346.7422 | 233
W14x211 | 15.75 | 1 | 15.75 | 1.5625 | 2.25 | 1.125 | na | na | 7.7083 | 2.3495 | 314.0026 | 211
W14x193 | 15.5 | 0.875 | 15.75 | 1.4375 | 2.125 | 1.0625 | na | na | 7.6875 | 2.3432 | 287.2157 | 193
W14x176 | 15.25 | 0.8125 | 15.625 | 1.3125 | 2 | 1.0625 | na | na | 7.6146 | 2.3209 | 261.9169 | 176
W14x159 | 15 | 0.75 | 15.625 | 1.1875 | 1.875 | 1 | na | na | 7.5833 | 2.3114 | 236.6181 | 159
W14x145 | 14.75 | 0.6875 | 15.5 | 1.0625 | 1.75 | 1 | na | na | 7.5104 | 2.2892 | 215.7838 | 145
W14x132 | 14.625 | 0.625 | 14.75 | 1 | 1.6875 | 0.9375 | 5.5 | 3 | 7.25 | 2.2098 | 196.4377 | 132
W14x120 | 14.5 | 0.5625 | 14.625 | 0.9375 | 1.625 | 0.9375 | 5.5 | 3 | 7.1979 | 2.1939 | 178.5797 | 120
W14x109 | 14.375 | 0.5 | 14.625 | 0.875 | 1.5625 | 0.875 | 5.5 | 2.75 | 7.1875 | 2.1908 | 162.2099 | 109
W14x99 | 14.125 | 0.5 | 14.625 | 0.75 | 1.4375 | 0.875 | 5.5 | 2.75 | 7.1458 | 2.1781 | 147.3282 | 99
W14x90 | 14 | 0.4375 | 14.5 | 0.6875 | 1.375 | 0.875 | 5.5 | 2.75 | 7.0938 | 2.1622 | 133.9348 | 90
W14x82 | 14.25 | 0.5 | 10.125 | 0.875 | 1.625 | 1 | 5.5 | 2.75 | 5.6667 | 1.7272 | 122.0295 | 82
W14x74 | 14.125 | 0.4375 | 10.125 | 0.8125 | 1.5625 | 0.9375 | 5.5 | 2.75 | 5.6562 | 1.724 | 110.1241 | 74
W14x68 | 14 | 0.4375 | 10 | 0.75 | 1.5 | 0.9375 | 5.5 | 2.75 | 5.5938 | 1.705 | 101.1952 | 68
W14x61 | 13.875 | 0.375 | 10 | 0.625 | 1.4375 | 0.9375 | 5.5 | 2.75 | 5.5833 | 1.7018 | 90.778 | 61
W14x53 | 13.875 | 0.375 | 8 | 0.6875 | 1.4375 | 0.9375 | 5.5 | 2.75 | 4.9167 | 1.4986 | 78.8727 | 53
W14x48 | 13.75 | 0.3125 | 8 | 0.625 | 1.375 | 0.875 | 5.5 | 2.5 | 4.9062 | 1.4954 | 71.4319 | 48
W14x43 | 13.625 | 0.3125 | 8 | 0.5 | 1.3125 | 0.875 | 5.5 | 2.5 | 4.8854 | 1.4891 | 63.9911 | 43
W14x38 | 14.125 | 0.3125 | 6.75 | 0.5 | 1.0625 | 0.625 | 3.5 | 2.5 | 4.5521 | 1.3875 | 56.5502 | 38
W14x34 | 14 | 0.3125 | 6.75 | 0.4375 | 1 | 0.625 | 3.5 | 2.5 | 4.5312 | 1.3811 | 50.5976 | 34
W14x30 | 13.875 | 0.25 | 6.75 | 0.375 | 0.9375 | 0.625 | 3.5 | 2.5 | 4.5208 | 1.378 | 44.6449 | 30
W14x26 | 13.875 | 0.25 | 5 | 0.4375 | 0.9375 | 0.5625 | 2.75 | 2.5 | 3.9375 | 1.2002 | 38.6923 | 26
W14x22 | 13.75 | 0.25 | 5 | 0.3125 | 0.875 | 0.5625 | 2.75 | 2.25 | 3.9167 | 1.1938 | 32.7396 | 22
W12x336 | 16.875 | 1.75 | 13.375 | 2.9375 | 3.6875 | 1.5 | na | na | 6.9792 | 2.1273 | 500.0231 | 336
W12x305 | 16.375 | 1.625 | 13.25 | 2.6875 | 3.4375 | 1.4375 | na | na | 6.875 | 2.0955 | 453.89 | 305
W12x279 | 15.875 | 1.5 | 13.125 | 2.5 | 3.1875 | 1.375 | na | na | 6.7708 | 2.0638 | 415.1978 | 279
W12x252 | 15.375 | 1.375 | 13 | 2.25 | 2.9375 | 1.3125 | na | na | 6.6667 | 2.032 | 375.0173 | 252
W12x230 | 15 | 1.3125 | 12.875 | 2.0625 | 2.75 | 1.25 | na | na | 6.5729 | 2.0034 | 342.2777 | 230
W12x210 | 14.75 | 1.1875 | 12.75 | 1.875 | 2.625 | 1.25 | na | na | 6.5104 | 1.9844 | 312.5144 | 210
W12x190 | 14.375 | 1.0625 | 12.625 | 1.75 | 2.4375 | 1.1875 | na | na | 6.4271 | 1.959 | 282.7512 | 190
W12x170 | 14 | 0.9375 | 12.625 | 1.5625 | 2.25 | 1.125 | na | na | 6.3854 | 1.9463 | 252.9879 | 170
W12x152 | 13.75 | 0.875 | 12.5 | 1.375 | 2.125 | 1.0625 | na | na | 6.3125 | 1.9241 | 226.2009 | 152
W12x136 | 13.375 | 0.8125 | 12.375 | 1.25 | 1.9375 | 1 | na | na | 6.2188 | 1.8955 | 202.3903 | 136
W12x120 | 13.125 | 0.6875 | 12.375 | 1.125 | 1.8125 | 1 | 5.5 | 3 | 6.1979 | 1.8891 | 178.5797 | 120
W12x106 | 12.875 | 0.625 | 12.25 | 1 | 1.6875 | 0.9375 | 5.5 | 3 | 6.125 | 1.8669 | 157.7454 | 106
W12x96 | 12.75 | 0.5625 | 12.125 | 0.875 | 1.625 | 0.875 | 5.5 | 3 | 6.0729 | 1.851 | 142.8637 | 96
W12x87 | 12.5 | 0.5 | 12.125 | 0.8125 | 1.5 | 0.875 | 5.5 | 2.75 | 6.0417 | 1.8415 | 129.4703 | 87
W12x79 | 12.375 | 0.5 | 12.125 | 0.75 | 1.4375 | 0.875 | 5.5 | 2.75 | 6.0208 | 1.8352 | 117.565 | 79
W12x72 | 12.25 | 0.4375 | 12 | 0.6875 | 1.375 | 0.875 | 5.5 | 2.75 | 5.9688 | 1.8193 | 107.1478 | 72
W12x65 | 12.125 | 0.375 | 12 | 0.625 | 1.3125 | 0.8125 | 5.5 | 2.5 | 5.9583 | 1.8161 | 96.7307 | 65
W12x58 | 12.25 | 0.375 | 10 | 0.625 | 1.375 | 0.8125 | 5.5 | 2.75 | 5.3125 | 1.6193 | 86.3135 | 58
W12x53 | 12 | 0.375 | 10 | 0.5625 | 1.25 | 0.8125 | 5.5 | 2.5 | 5.2708 | 1.6066 | 78.8727 | 53
W12x50 | 12.25 | 0.375 | 8.125 | 0.625 | 1.375 | 0.8125 | 5.5 | 2.75 | 4.6875 | 1.4288 | 74.4082 | 50
W12x45 | 12 | 0.3125 | 8 | 0.5625 | 1.25 | 0.8125 | 5.5 | 2.5 | 4.6146 | 1.4065 | 66.9674 | 45
W12x40 | 12 | 0.3125 | 8 | 0.5 | 1.25 | 0.75 | 5.5 | 2.5 | 4.6146 | 1.4065 | 59.5266 | 40
W12x35 | 12.5 | 0.3125 | 6.5 | 0.5 | 1 | 0.5625 | 3.5 | 2.5 | 4.1979 | 1.2795 | 52.0857 | 35
W12x30 | 12.375 | 0.25 | 6.5 | 0.4375 | 0.9375 | 0.5 | 3.5 | 2.5 | 4.1875 | 1.2764 | 44.6449 | 30
W12x26 | 12.25 | 0.25 | 6.5 | 0.375 | 0.875 | 0.5 | 3.5 | 2.5 | 4.1667 | 1.27 | 38.6923 | 26
W12x22 | 12.25 | 0.25 | 4 | 0.4375 | 0.875 | 0.5 | 2.25 | 2.5 | 3.3333 | 1.016 | 32.7396 | 22
W12x19 | 12.125 | 0.25 | 4 | 0.375 | 0.8125 | 0.5 | 2.25 | 2.25 | 3.3125 | 1.0097 | 28.2751 | 19
W12x16 | 12 | 0.25 | 4 | 0.25 | 0.75 | 0.5 | 2.25 | 2.25 | 3.2917 | 1.0033 | 23.8106 | 16
W12x14 | 11.875 | 0.1875 | 4 | 0.25 | 0.6875 | 0.5 | 2.25 | 2.25 | 3.2812 | 1.0001 | 20.8343 | 14
W10x112 | 11.375 | 0.75 | 10.375 | 1.25 | 1.875 | 0.9375 | na | na | 5.2292 | 1.5939 | 166.6744 | 112
W10x100 | 11.125 | 0.6875 | 10.375 | 1.125 | 1.75 | 0.875 | na | na | 5.1979 | 1.5843 | 148.8164 | 100
W10x88 | 10.875 | 0.625 | 10.25 | 1 | 1.625 | 0.8125 | 5.5 | 2.75 | 5.125 | 1.5621 | 130.9584 | 88
W10x77 | 10.625 | 0.5 | 10.25 | 0.875 | 1.5 | 0.8125 | 5.5 | 2.75 | 5.1042 | 1.5558 | 114.5886 | 77
W10x68 | 10.375 | 0.5 | 10.125 | 0.75 | 1.375 | 0.75 | 5.5 | 2.75 | 5.0208 | 1.5304 | 101.1952 | 68
W10x60 | 10.25 | 0.4375 | 10.125 | 0.6875 | 1.3125 | 0.75 | 5.5 | 2.5 | 5.0104 | 1.5272 | 89.2898 | 60
W10x54 | 10.125 | 0.375 | 10 | 0.625 | 1.25 | 0.6875 | 5.5 | 2.5 | 4.9583 | 1.5113 | 80.3609 | 54
W10x49 | 10 | 0.3125 | 10 | 0.5625 | 1.1875 | 0.6875 | 5.5 | 2.5 | 4.9479 | 1.5081 | 72.92 | 49
W10x45 | 10.125 | 0.375 | 8 | 0.625 | 1.25 | 0.6875 | 5.5 | 2.5 | 4.2917 | 1.3081 | 66.9674 | 45
W10x39 | 9.875 | 0.3125 | 8 | 0.5 | 1.125 | 0.6875 | 5.5 | 2.5 | 4.2604 | 1.2986 | 58.0384 | 39
W10x33 | 9.75 | 0.3125 | 8 | 0.4375 | 1.0625 | 0.6875 | 5.5 | 2.25 | 4.2396 | 1.2922 | 49.1094 | 33
W10x30 | 10.5 | 0.3125 | 5.75 | 0.5 | 0.9375 | 0.5 | 2.75 | 2.5 | 3.6146 | 1.1017 | 44.6449 | 30
W10x26 | 10.375 | 0.25 | 5.75 | 0.4375 | 0.875 | 0.5 | 2.75 | 2.25 | 3.6042 | 1.0986 | 38.6923 | 26
W10x22 | 10.125 | 0.25 | 5.75 | 0.375 | 0.75 | 0.5 | 2.75 | 2.25 | 3.5625 | 1.0859 | 32.7396 | 22
W10x19 | 10.25 | 0.25 | 4 | 0.375 | 0.8125 | 0.5 | 2.25 | 2.25 | 3 | 0.9144 | 28.2751 | 19
W10x17 | 10.125 | 0.25 | 4 | 0.3125 | 0.75 | 0.5 | 2.25 | 2.25 | 2.9792 | 0.90805 | 25.2988 | 17
W10x15 | 10 | 0.25 | 4 | 0.25 | 0.6875 | 0.4375 | 2.25 | 2.25 | 2.9583 | 0.9017 | 22.3225 | 15
W10x12 | 9.875 | 0.1875 | 4 | 0.1875 | 0.625 | 0.4375 | 2.25 | 2 | 2.9479 | 0.89853 | 17.858 | 12
W8x67 | 9 | 0.5625 | 8.25 | 0.9375 | 1.4375 | 0.6875 | na | na | 4.1562 | 1.2668 | 99.707 | 67
W8x58 | 8.75 | 0.5 | 8.25 | 0.8125 | 1.3125 | 0.6875 | 5.5 | 2.75 | 4.125 | 1.2573 | 86.3135 | 58
W8x48 | 8.5 | 0.375 | 8.125 | 0.6875 | 1.1875 | 0.625 | 5.5 | 2.5 | 4.0625 | 1.2383 | 71.4319 | 48
W8x40 | 8.25 | 0.375 | 8.125 | 0.5625 | 1.0625 | 0.625 | 5.5 | 2.5 | 4.0208 | 1.2256 | 59.5266 | 40
W8x35 | 8.125 | 0.3125 | 8 | 0.5 | 1 | 0.5625 | 5.5 | 2.25 | 3.9688 | 1.2097 | 52.0857 | 35
W8x31 | 8 | 0.3125 | 8 | 0.4375 | 0.9375 | 0.5625 | 5.5 | 2.25 | 3.9479 | 1.2033 | 46.1331 | 31
W8x28 | 8 | 0.3125 | 6.5 | 0.4375 | 0.9375 | 0.5625 | 3.5 | 2.25 | 3.4479 | 1.0509 | 41.6686 | 28
W8x24 | 7.875 | 0.25 | 6.5 | 0.375 | 0.875 | 0.5625 | 3.5 | 2.25 | 3.4375 | 1.0478 | 35.7159 | 24
W8x21 | 8.25 | 0.25 | 5.25 | 0.375 | 0.8125 | 0.5 | 2.75 | 2.25 | 3.0833 | 0.9398 | 31.2514 | 21
W8x18 | 8.125 | 0.25 | 5.25 | 0.3125 | 0.75 | 0.4375 | 2.75 | 2.25 | 3.0625 | 0.93345 | 26.787 | 18
W8x15 | 8.125 | 0.25 | 4 | 0.3125 | 0.75 | 0.5 | 2.25 | 2.25 | 2.6458 | 0.80645 | 22.3225 | 15
W8x13 | 8 | 0.25 | 4 | 0.25 | 0.6875 | 0.4375 | 2.25 | 2.25 | 2.625 | 0.8001 | 19.3461 | 13
W8x10 | 7.875 | 0.1875 | 4 | 0.1875 | 0.625 | 0.4375 | 2.25 | 2 | 2.6146 | 0.79693 | 14.8816 | 10
W6x25 | 6.375 | 0.3125 | 6.125 | 0.4375 | 0.8125 | 0.4375 | 3.5 | 2.25 | 3.0521 | 0.93028 | 37.2041 | 25
W6x20 | 6.25 | 0.25 | 6 | 0.375 | 0.75 | 0.4375 | 3.5 | 2.25 | 3 | 0.9144 | 29.7633 | 20
W6x15 | 6 | 0.25 | 6 | 0.25 | 0.625 | 0.375 | 3.5 | 2.25 | 2.9583 | 0.9017 | 22.3225 | 15
W6x16 | 6.25 | 0.25 | 4 | 0.375 | 0.75 | 0.4375 | 2.25 | 2.25 | 2.3333 | 0.7112 | 23.8106 | 16
W6x12 | 6 | 0.25 | 4 | 0.25 | 0.625 | 0.375 | 2.25 | 2.25 | 2.2917 | 0.6985 | 17.858 | 12
W6x9 | 5.875 | 0.1875 | 4 | 0.1875 | 0.5625 | 0.375 | 2.25 | 2 | 2.2812 | 0.69533 | 13.3935 | 9
W5x19 | 5.125 | 0.25 | 5 | 0.4375 | 0.8125 | 0.4375 | 2.75 | 2.25 | 2.4792 | 0.75565 | 28.2751 | 19
W5x16 | 5 | 0.25 | 5 | 0.375 | 0.75 | 0.4375 | 2.75 | 2.25 | 2.4583 | 0.7493 | 23.8106 | 16
W4x13 | 4.125 | 0.25 | 4 | 0.375 | 0.6875 | 0.4375 | 2.25 | 2 | 1.9792 | 0.60325 | 19.3461 | 13

## M Shapes
2017-06-13 14:31
Flg. Width "bf"
|  | M Shapes |  |  |  |  | Flg Gage
k1
|  |  |  | Flg. Thk "tf" | [5 empty] | k
Web Gage
Depth
"d"
Web thk. "tw"
Beam | Depth | Web Thk. | Flg. Width | Flg. Thk. | k | Max | Flange | Web | Sq. Ft.- Surf | Sq.M.- Surf | Weight
Size | d | tw | bf | tf |  | Bolt | Bolt Gage | Bolt Gage | Area - per Ft | Area - per M | Kg per M
M14x18 | 14 | 0.1875 | 4 | 0.25 | 0.625 | 0.75 |  |  | 3.6354 | 1.1081 | 26.787 | 18
M12x11.8 | 12 | 0.1875 | 3.125 | 0.25 | 0.5625 | - |  |  | 3.0104 | 0.91758 | 17.5603 | 11.8
M12x10.8 | 12 | 0.1875 | 3.125 | 0.25 | 0.5 | 0.5 |  |  | 3.0104 | 0.91758 | 16.0722 | 10.8
M12x10 | 12 | 0.1875 | 3.25 | 0.1875 | 0.5 |  |  |  | 3.0521 | 0.93028 | 14.8816 | 10
M10x9 | 10 | 0.1875 | 2.75 | 0.1875 | 0.5625 | - |  |  | 2.5521 | 0.77788 | 13.3935 | 9
M10x8 | 10 | 0.1875 | 2.75 | 0.1875 | 0.4375 | 0.375 |  |  | 2.5521 | 0.77788 | 11.9053 | 8
M10x7.5 | 10 | 0.125 | 2.75 | 0.1875 | 0.4375 | 0.375 |  |  | 2.5625 | 0.78105 | 11.1612 | 7.5
M8x6.5 | 8 | 0.125 | 2.25 | 0.1875 | 0.5 | - |  |  | 2.0625 | 0.62865 | 9.6731 | 6.5
M6x4.4 | 6 | 0.125 | 1.875 | 0.1875 | 0.1875 | - |  |  | 1.6042 | 0.48895 | 6.5479 | 4.4
M5x18.9 | 5 | 0.3125 | 5 | 0.4375 | 0.875 | 0.875 |  |  | 2.4479 | 0.74613 | 28.1263 | 18.9

## S Shapes
2017-06-13 14:31
Flg. Width "bf"
| S Shapes |  |  |  |  | Flg Gage
|  | Avg. Flg. Thk "tf" | [6 empty] | " k"
Web Gage
Depth
"d"
Web thk. "tw"
** Flg. Slope 1:6
Beam | Depth | Web Thk. | Flg. Width | *Flg. Thk. | k | Grip | Max | Flange | Web | Sq. Ft.- Surf | Sq.M.- Surf | Weight
Size | d | tw | bf | tf |  |  | Bolt | Bolt Gage | Bolt Gage | Area - per Ft | Area - per M | Kg per M
S24x121 | 24.5 | 0.8125 | 8 | 1.0625 | 2 | 1.125 | 1 |  |  | 6.6146 | 2.0161 | 180.0678 | 121
S24x106 | 24.5 | 0.625 | 7.875 | 1.0625 | 2 | 1.125 | 1 |  |  | 6.6042 | 2.013 | 157.7454 | 106
S24x100 | 24 | 0.75 | 7.25 | 0.875 | 1.75 | 0.875 | 1 | 4 | 3 | 6.2917 | 1.9177 | 148.8164 | 100
S24x90 | 24 | 0.625 | 7.125 | 0.875 | 1.75 | 0.875 | 1 | 4 | 3 | 6.2708 | 1.9114 | 133.9348 | 90
S24x80 | 24 | 0.5 | 7 | 0.875 | 1.75 | 0.875 | 1 |  |  | 6.25 | 1.905 | 119.0531 | 80
S20x96 | 20.25 | 0.8125 | 7.25 | 0.9375 | 1.75 | 0.9375 | 1 |  |  | 5.6562 | 1.724 | 142.8637 | 96
S20x86 | 20.25 | 0.6875 | 7 | 0.9375 | 1.75 | 0.9375 | 1 |  |  | 5.5938 | 1.705 | 127.9821 | 86
S20x75 | 20 | 0.625 | 6.375 | 0.8125 | 1.625 | 0.8125 | 0.875 | 3.5 | 3 | 5.3542 | 1.632 | 111.6123 | 75
S20x66 | 20 | 0.5 | 6.25 | 0.8125 | 1.625 | 0.8125 | 0.875 |  |  | 5.3333 | 1.6256 | 98.2188 | 66
S18x70 | 18 | 0.6875 | 6.25 | 0.6875 | 1.5 | 0.6875 | 0.875 | 3.5 | 2.75 | 4.9688 | 1.5145 | 104.1715 | 70
S18x54.7 | 18 | 0.4375 | 6 | 0.6875 | 1.5 | 0.6875 | 0.875 | 3.5 | 2.75 | 4.9271 | 1.5018 | 81.4026 | 54.7
S15x50 | 15 | 0.5625 | 5.625 | 0.625 | 1.375 | 0.5625 | 0.75 | 3.5 | 2.75 | 4.2812 | 1.3049 | 74.4082 | 50
S15x42.9 | 15 | 0.4375 | 5.5 | 0.625 | 1.375 | 0.5625 | 0.75 | 3.5 | 2.75 | 4.2604 | 1.2986 | 63.8422 | 42.9
S12x50 | 12 | 0.6875 | 5.5 | 0.6875 | 1.4375 | 0.6875 | 0.75 | 3 | 2.75 | 3.7188 | 1.1335 | 74.4082 | 50
S12x40.8 | 12 | 0.4375 | 5.25 | 0.6875 | 1.4375 | 0.625 | 0.75 | 3 | 2.75 | 3.6771 | 1.1208 | 60.7171 | 40.8
S12x35 | 12 | 0.4375 | 5.125 | 0.5625 | 1.1875 | 0.5 | 0.75 | 3 | 2.5 | 3.6354 | 1.1081 | 52.0857 | 35
S12x31.8 | 12 | 0.375 | 5 | 0.5625 | 1.1875 | 0.5 | 0.75 | 3 | 2.5 | 3.6042 | 1.0986 | 47.3236 | 31.8
S10x35 | 10 | 0.625 | 5 | 0.5 | 1.125 | 0.5 | 0.75 | 2.75 | 2.5 | 3.2292 | 0.98425 | 52.0857 | 35
S10x25.4 | 10 | 0.3125 | 4.625 | 0.5 | 1.125 | 0.5 | 0.75 | 2.75 | 2.5 | 3.1562 | 0.96203 | 37.7994 | 25.4
S8x23 | 8 | 0.4375 | 4.125 | 0.4375 | 1 | 0.4375 | 0.75 | 2.25 | 2.5 | 2.6354 | 0.80328 | 34.2278 | 23
S8x18.4 | 8 | 0.25 | 4 | 0.4375 | 1 | 0.4375 | 0.75 | 2.25 | 2.5 | 2.625 | 0.8001 | 27.3822 | 18.4
S7x20 | 7 | 0.4375 | 3.875 | 0.375 | 0.9375 | 0.375 | 0.625 |  |  | 2.3854 | 0.72708 | 29.7633 | 20
S7x15.3 | 7 | 0.25 | 3.625 | 0.375 | 0.9375 | 0.375 | 0.625 | 2.25 | 2.5 | 2.3333 | 0.7112 | 22.7689 | 15.3
S6x17.25 | 6 | 0.4375 | 3.625 | 0.375 | 0.875 | 0.375 | 0.625 | 2 | 2.25 | 2.1354 | 0.65088 | 25.6708 | 17.25
S6x12.5 | 6 | 0.25 | 3.375 | 0.375 | 0.875 | 0.375 | - | - | 2.25 | 2.0833 | 0.635 | 18.6021 | 12.5
S5x14.75 | 5 | 0.5 | 3.25 | 0.3125 | 0.8125 | 0.3125 | - |  |  | 1.8333 | 0.5588 | 21.9504 | 14.75
S5x10 | 5 | 0.1875 | 3 | 0.3125 | 0.8125 | 0.3125 | - | - | 2.25 | 1.8021 | 0.54928 | 14.8816 | 10
S4x9.5 | 4 | 0.3125 | 2.75 | 0.3125 | 0.75 | 0.3125 | - | - | 2 | 1.5312 | 0.46673 | 14.1376 | 9.5
S4x7.7 | 4 | 0.1875 | 2.625 | 0.3125 | 0.75 | 0.3125 | - | - | 2 | 1.5104 | 0.46038 | 11.4589 | 7.7
S3x7.5 | 3 | 0.375 | 2.5 | 0.25 | 0.6875 | 0.25 | - | - | - | 1.2708 | 0.38735 | 11.1612 | 7.5
S3x5.7 | 3 | 0.1875 | 2.375 | 0.25 | 0.6875 | 0.25 | - | - | - | 1.2604 | 0.38418 | 8.4825 | 5.7

## HP Shapes
2017-06-13 14:31 |  |  |  |  | Flg. Width "bf"
Flg Gage
HP Shapes |  |  |  |  | k1
|  | Flg. Thk "tf" | [5 empty] | k
Web Gage
Depth
"d"
Web thk. "tw"
Beam | Depth | Web Thk. | Flg. Width | Flg. Thk. | k | k1 | Sq. Ft.- Surf | Sq.M.- Surf | Weight
Size | d | tw | bf | tf |  |  | Area - per Ft | Area - per M | Kg per M
HP14x117 | 14.25 | 0.8125 | 14.875 | 0.8125 | 1.5 | 1.0625 | 7.1979 | 2.1939 | 174.1152 | 117
HP14x102 | 14 | 0.6875 | 14.75 | 0.6875 | 1.375 | 1 | 7.1354 | 2.1749 | 151.7927 | 102
HP14x89 | 13.875 | 0.625 | 14.75 | 0.625 | 1.3125 | 0.9375 | 7.125 | 2.1717 | 132.4466 | 89
HP14x73 | 13.625 | 0.5 | 14.625 | 0.5 | 1.1875 | 0.875 | 7.0625 | 2.1527 | 108.636 | 73
HP13x100 | 13.125 | 0.75 | 13.25 | 0.75 | 1.4375 | 1 | 6.4792 | 1.9749 | 148.8164 | 100
HP13x87 | 13 | 0.6875 | 13.125 | 0.6875 | 1.375 | 0.9375 | 6.4271 | 1.959 | 129.4703 | 87
HP13x73 | 12.75 | 0.5625 | 13 | 0.5625 | 1.25 | 0.9375 | 6.3646 | 1.9399 | 108.636 | 73
HP13x60 | 12.5 | 0.4375 | 12.875 | 0.4375 | 1.125 | 0.875 | 6.3021 | 1.9209 | 89.2898 | 60
HP12x84 | 12.25 | 0.6875 | 12.25 | 0.6875 | 1.375 | 1 | 6.0104 | 1.832 | 125.0058 | 84
HP12x74 | 12.125 | 0.625 | 12.25 | 0.625 | 1.3125 | 0.9375 | 6 | 1.8288 | 110.1241 | 74
HP12x63 | 12 | 0.5 | 12.125 | 0.5 | 1.25 | 0.875 | 5.9583 | 1.8161 | 93.7543 | 63
HP12x53 | 11.75 | 0.4375 | 12 | 0.4375 | 1.125 | 0.875 | 5.8854 | 1.7939 | 78.8727 | 53
HP10x57 | 10 | 0.5625 | 10.25 | 0.5625 | 1.1875 | 0.8125 | 4.9896 | 1.5208 | 84.8254 | 57
HP10x42 | 9.75 | 0.4375 | 10.125 | 0.4375 | 1.0625 | 0.75 | 4.9271 | 1.5018 | 62.5029 | 42
HP8x36 | 8 | 0.4375 | 8.125 | 0.4375 | 0.9375 | 0.625 | 3.9688 | 1.2097 | 53.5739 | 36

## Channels
2017-06-13 14:31
Flg. Width "bf"
Flg Gage
|  |  |  | "k" |  |  |  |  | Avg. Flg. Thk.
Channels | [8 empty] | Web Gage
Standard
Depth
"d"
Web thk. "tw"
** Flg. Slope 1:6
Channel | Depth | Web Thk. | Flg. Width | Avg. Flg. Thk. | k | Grip | Max. | Flange | Web | Sq. Ft.- Surf | Sq.M.- Surf | Weight
Size | d | tw | bf | tf |  |  | Bolt | Bolt Gage | Bolt Gage | Area - per Ft | Area - per M | Kg per M
C15x50 | 15 | 0.6875 | 3.75 | 0.625 | 1.4375 | 0.625 | 1 | 2.25 | 2.75 | 3.5312 | 1.0763 | 74.4082 | 50
C15x40 | 15 | 0.5 | 3.5 | 0.625 | 1.4375 | 0.625 | 1 | 2 | 2.75 | 3.4792 | 1.0605 | 59.5266 | 40
C15x33.9 | 15 | 0.375 | 3.375 | 0.625 | 1.4375 | 0.625 | 1 | 2 | 2.75 | 3.4583 | 1.0541 | 50.4488 | 33.9
C12x30 | 12 | 0.5 | 3.125 | 0.5 | 1.125 | 0.5 | 0.875 | 1.75 | 2.5 | 2.875 | 0.8763 | 44.6449 | 30
C12x25 | 12 | 0.375 | 3 | 0.5 | 1.125 | 0.5 | 0.875 | 1.75 | 2.5 | 2.8542 | 0.86995 | 37.2041 | 25
C12x20.7 | 12 | 0.3125 | 3 | 0.5 | 1.125 | 0.5 | 0.875 | 1.75 | 2.5 | 2.8646 | 0.87313 | 30.805 | 20.7
C10X30 | 10 | 0.6875 | 3 | 0.4375 | 1 | 0.4375 | 0.75 | 1.75 | 2.5 | 2.4792 | 0.75565 | 44.6449 | 30
C10x25 | 10 | 0.5 | 2.875 | 0.4375 | 1 | 0.4375 | 0.75 | 1.75 | 2.5 | 2.4688 | 0.75248 | 37.2041 | 25
C10x20 | 10 | 0.375 | 2.75 | 0.4375 | 1 | 0.4375 | 0.75 | 1.5 | 2.5 | 2.4479 | 0.74613 | 29.7633 | 20
C10x15.3 | 10 | 0.25 | 2.625 | 0.4375 | 1 | 0.4375 | 0.75 | 1.5 | 2.5 | 2.4271 | 0.73978 | 22.7689 | 15.3
C9x20 | 9 | 0.4375 | 2.625 | 0.4375 | 0.9375 | 0.4375 | 0.75 |  |  | 2.2292 | 0.67945 | 29.7633 | 20
C9x15 | 9 | 0.3125 | 2.5 | 0.4375 | 0.9375 | 0.4375 | 0.75 | 1.375 | 2.5 | 2.2083 | 0.6731 | 22.3225 | 15
C9x13.4 | 9 | 0.25 | 2.375 | 0.4375 | 0.9375 | 0.4375 | 0.75 | 1.375 | 2.5 | 2.1771 | 0.66358 | 19.9414 | 13.4
C8x18.75 | 8 | 0.5 | 2.5 | 0.375 | 0.9375 | 0.375 | 0.75 | 1.5 | 2.5 | 2.0208 | 0.61595 | 27.9031 | 18.75
C8x13.75 | 8 | 0.3125 | 2.375 | 0.375 | 0.9375 | 0.375 | 0.75 | 1.375 | 2.5 | 2.0104 | 0.61278 | 20.4623 | 13.75
C8x11.5 | 8 | 0.25 | 2.25 | 0.375 | 0.9375 | 0.375 | 0.75 | 1.375 | 2.5 | 1.9792 | 0.60325 | 17.1139 | 11.5
C7x14.75 | 7 | 0.4375 | 2.25 | 0.375 | 0.875 | 0.375 | 0.625 | 1.25 | 2.5 | 1.7812 | 0.54293 | 21.9504 | 14.75
C7x12.25 | 7 | 0.3125 | 2.25 | 0.375 | 0.875 | 0.375 | 0.625 | 1.25 | 2.5 | 1.8021 | 0.54928 | 18.23 | 12.25
C7x9.8 | 7 | 0.1875 | 2.125 | 0.375 | 0.875 | 0.375 | 0.625 | 1.25 | 2.25 | 1.7812 | 0.54293 | 14.584 | 9.8
C6x13 | 6 | 0.4375 | 2.125 | 0.3125 | 0.8125 | 0.3125 | 0.625 | 1.375 | 2.25 | 1.5833 | 0.4826 | 19.3461 | 13
C6x10.5 | 6 | 0.3125 | 2 | 0.3125 | 0.8125 | 0.375 | 0.625 | 1.125 | 2.25 | 1.5625 | 0.47625 | 15.6257 | 10.5
C6x8.2 | 6 | 0.1875 | 1.875 | 0.3125 | 0.8125 | 0.3125 | 0.625 | 1.125 | 2.25 | 1.5417 | 0.4699 | 12.2029 | 8.2
C5x9 | 5 | 0.3125 | 1.875 | 0.3125 | 0.75 | 0.3125 | 0.625 | 1.125 | 2.25 | 1.3542 | 0.41275 | 13.3935 | 9
C5x6.7 | 5 | 0.1875 | 1.75 | 0.3125 | 0.75 | - | - | - | 2.25 | 1.3333 | 0.4064 | 9.9707 | 6.7
C4x7.25 | 4 | 0.3125 | 1.75 | 0.3125 | 0.6875 | 0.3125 | 0.625 | 1 | 2 | 1.1458 | 0.34925 | 10.7892 | 7.25
C4x5.4 | 4 | 0.1875 | 1.625 | 0.3125 | 0.6875 | - | - | - | 2 | 1.125 | 0.3429 | 8.0361 | 5.4
C3x6 | 3 | 0.375 | 1.625 | 0.25 | 0.6875 | - | - | - | - | 0.9375 | 0.28575 | 8.929 | 6
C3x5 | 3 | 0.25 | 1.5 | 0.25 | 0.6875 | - | - | - | - | 0.91667 | 0.2794 | 7.4408 | 5
C3x4.1 | 3 | 0.1875 | 1.375 | 0.25 | 0.6875 | - | - | - | - | 0.88542 | 0.26988 | 6.1015 | 4.1

## MC Channels
2017-06-13 14:31
Flg. Width "bf"
| Channels |  |  |  |  | Flg Gage
Miscellaneous
|  |  |  | "k" |  |  |  |  | Avg. Flg. Thk.
Web Gage
Depth
"d"
Web thk. "tw"
** Flg. Slope 1:6
Channel | Depth | Web Thk. | Flg. Width | Avg. Flg. Thk. | k | Grip | Max. | Flange | Web | Sq. Ft.- Surf | Sq.M.- Surf | Weight
Size | d | tw | bf | tf |  |  | Bolt | Bolt Gage | Bolt Gage | Area - per Ft | Area - per M | Kg per M
MC18x58 | 18 | 0.6875 | 4.25 | 0.625 | 1.375 | 0.625 | 1 |  |  | 4.1979 | 1.2795 | 86.3135 | 58
MC18x51.9 | 18 | 0.625 | 4.125 | 0.625 | 1.375 | 0.625 | 1 |  |  | 4.1667 | 1.27 | 77.2357 | 51.9
MC18x45.8 | 18 | 0.5 | 4 | 0.625 | 1.375 | 0.625 | 1 |  |  | 4.1458 | 1.2637 | 68.1579 | 45.8
MC18x42.7 | 18 | 0.4375 | 4 | 0.625 | 1.375 | 0.625 | 1 |  |  | 4.1562 | 1.2668 | 63.5446 | 42.7
MC13x50 | 13 | 0.8125 | 4.375 | 0.625 | 1.375 | 0.625 | 1 |  |  | 3.3854 | 1.0319 | 74.4082 | 50
MC13x40 | 13 | 0.5625 | 4.125 | 0.625 | 1.375 | 0.5625 | 1 |  |  | 3.3438 | 1.0192 | 59.5266 | 40
MC13x35 | 13 | 0.4375 | 4.125 | 0.625 | 1.375 | 0.5625 | 1 |  |  | 3.3646 | 1.0255 | 52.0857 | 35
MC13x31.8 | 13 | 0.375 | 4 | 0.625 | 1.375 | 0.5625 | 1 |  |  | 3.3333 | 1.016 | 47.3236 | 31.8
MC12x50 | 12 | 0.8125 | 4.125 | 0.6875 | 1.3125 | 0.6875 | 1 |  |  | 3.125 | 0.9525 | 74.4082 | 50
MC12x45 | 12 | 0.6875 | 4 | 0.6875 | 1.3125 | 0.6875 | 1 |  |  | 3.1042 | 0.94615 | 66.9674 | 45
MC12x40 | 12 | 0.5625 | 3.875 | 0.6875 | 1.3125 | 0.6875 | 1 |  |  | 3.0833 | 0.9398 | 59.5266 | 40
MC12x35 | 12 | 0.4375 | 3.75 | 0.6875 | 1.3125 | 0.6875 | 1 |  |  | 3.0625 | 0.93345 | 52.0857 | 35
MC12x31 | 12 | 0.375 | 3.625 | 0.6875 | 1.3125 | 0.6875 | 1 |  |  | 3.0312 | 0.92393 | 46.1331 | 31
MC12x10.6 | 12 | 0.1875 | 1.5 | 0.3125 | 0.6875 | - | - |  |  | 2.4167 | 0.7366 | 15.7745 | 10.6
MC10x41.1 | 10 | 0.8125 | 4.375 | 0.5625 | 1.25 | 0.5625 | 0.875 |  |  | 2.8958 | 0.88265 | 61.1635 | 41.1
MC10x33.6 | 10 | 0.5625 | 4.125 | 0.5625 | 1.25 | 0.5625 | 0.875 |  |  | 2.8542 | 0.86995 | 50.0023 | 33.6
MC10x28.5 | 10 | 0.4375 | 4 | 0.5625 | 1.25 | 0.5625 | 0.875 |  |  | 2.8333 | 0.8636 | 42.4127 | 28.5
MC10x25 | 10 | 0.375 | 3.375 | 0.5625 | 1.25 | 0.5625 | 0.875 |  |  | 2.6354 | 0.80328 | 37.2041 | 25
MC10x22 | 10 | 0.3125 | 3.375 | 0.5625 | 1.25 | 0.5625 | 0.875 |  |  | 2.6458 | 0.80645 | 32.7396 | 22
MC10x8.4 | 10 | 0.1875 | 1.5 | 0.25 | 0.6875 | - | - |  |  | 2.0938 | 0.63818 | 12.5006 | 8.4
MC10x6.5 | 10 | 0.125 | 1.125 | 0.1875 | 0.4375 | - | - |  |  | 1.9896 | 0.60643 | 9.6731 | 6.5
MC9x25.4 | 9 | 0.4375 | 3.5 | 0.5625 | 1.1875 | 0.5625 | 0.875 |  |  | 2.5 | 0.762 | 37.7994 | 25.4
MC9x23.9 | 9 | 0.375 | 3.5 | 0.5625 | 1.1875 | 0.5625 | 0.875 |  |  | 2.5104 | 0.76518 | 35.5671 | 23.9
MC8x22.8 | 8 | 0.4375 | 3.5 | 0.5 | 1.1875 | 0.5 | 0.875 |  |  | 2.3438 | 0.71438 | 33.9301 | 22.8
MC8x21.4 | 8 | 0.375 | 3.5 | 0.5 | 1.1875 | 0.5 | 0.875 |  |  | 2.3542 | 0.71755 | 31.8467 | 21.4
MC8x20 | 8 | 0.375 | 3 | 0.5 | 1.125 | 0.5 | 0.875 |  |  | 2.1875 | 0.66675 | 29.7633 | 20
MC8x18.7 | 8 | 0.375 | 3 | 0.5 | 1.1875 | 0.5 | 0.875 |  |  | 2.1875 | 0.66675 | 27.8287 | 18.7
MC8x8.5 | 8 | 0.1875 | 1.875 | 0.3125 | 0.75 | 0.3125 | 0.625 |  |  | 1.875 | 0.5715 | 12.6494 | 8.5
MC7x22.7 | 7 | 0.5 | 3.625 | 0.5 | 1.125 | 0.5 | 0.875 |  |  | 2.2083 | 0.6731 | 33.7813 | 22.7
MC7x19.1 | 7 | 0.375 | 3.5 | 0.5 | 1.125 | 0.5 | 0.875 |  |  | 2.1875 | 0.66675 | 28.4239 | 19.1
MC6x18 | 6 | 0.375 | 3.5 | 0.5 | 1.0625 | 0.5 | 0.875 |  |  | 2.0208 | 0.61595 | 26.787 | 18
MC6x15.3 | 6 | 0.3125 | 3.5 | 0.375 | 0.875 | 0.375 | 0.875 |  |  | 2.0521 | 0.62548 | 22.7689 | 15.3
MC6x16.3 | 6 | 0.375 | 3 | 0.5 | 1.0625 | 0.5 | 0.75 |  |  | 1.8542 | 0.56515 | 24.2571 | 16.3
MC6x15.1 | 6 | 0.3125 | 3 | 0.5 | 1.0625 | 0.5 | 0.75 |  |  | 1.8646 | 0.56833 | 22.4713 | 15.1
MC6x12 | 6 | 0.3125 | 2.5 | 0.375 | 0.8125 | 0.375 | 0.625 |  |  | 1.7188 | 0.52388 | 17.858 | 12

## Angles
Angles |  |  |  |  | g
2017-06-13 14:31
g1
g2
Usual Gages For Angles , Inches
Leg | 8 | 7 | 6 | 5 | 4 | 3.5 | 3 | 2.5 | 2 | 1.75 | 1.375 | 1.25 | 1
g | 4.5 | 4 | 3.5 | 3 | 2.5 | 2 | 1.75 | 1.375 | 1.125 | 1 | 0.875 | 0.75 | 0.625
g1 | 3 | 2.5 | 2.25 | 2
g2 | 3 | 3 | 2.5 | 1.75
Angles in shaded rows may not be readily available
Size | Thk. | k | Weight | Weight | Surf. Area | Surf. Area |  | Size | Thk. | k | Weight | Weight | Surf. Area | Surf. Area
|  |  | lbs/ft | Kg per M | Sq.Ft-Ft. | Sq.M-M. |  |  |  |  | lbs/ft | Kg per M | Sq.Ft-Ft. | Sq.M-M.
L9x4 | 0.625 | 1.125 | 26.3 | 39.1387 | 2.1667 | 0.6604 |  | L4x3 1/2 | 0.5 | 0.9375 | 11.9 | 17.7092 | 1.25 | 0.381 | 9 | 4 | 4 | 3.5
L9x4 | 0.5625 | 1.0625 | 23.8 | 35.4183 | 2.1667 | 0.6604 |  | L4x3 1/2 | 0.4375 | 0.875 | 10.6 | 15.7745 | 1.25 | 0.381 | 9 | 4 | 4 | 3.5
L9x4 | 0.5 | 1 | 21.3 | 31.6979 | 2.1667 | 0.6604 |  | L4x3 1/2 | 0.375 | 0.8125 | 9.1 | 13.5423 | 1.25 | 0.381 | 9 | 4 | 4 | 3.5
[8 empty] | L4x3 1/2 | 0.3125 | 0.75 | 7.7 | 11.4589 | 1.25 | 0.381 |  |  | 4 | 3.5
L8x8 | 1.125 | 1.75 | 56.9 | 84.6765 | 2.6667 | 0.8128 |  | L4x3 1/2 | 0.25 | 0.6875 | 6.2 | 9.2266 | 1.25 | 0.381 | 8 | 8 | 4 | 3.5
L8x8 | 1 | 1.625 | 51 | 75.8964 | 2.6667 | 0.8128 | [8 empty] | 8 | 8
L8x8 | 0.875 | 1.5 | 45 | 66.9674 | 2.6667 | 0.8128 |  | L4x3 | 0.5 | 0.9375 | 11.1 | 16.5186 | 1.1667 | 0.3556 | 8 | 8 | 4 | 3
L8x8 | 0.75 | 1.375 | 38.9 | 57.8896 | 2.6667 | 0.8128 |  | L4x3 | 0.4375 | 0.875 | 9.8 | 14.584 | 1.1667 | 0.3556 | 8 | 8 | 4 | 3
L8x8 | 0.625 | 1.25 | 32.7 | 48.663 | 2.6667 | 0.8128 |  | L4x3 | 0.375 | 0.8125 | 8.5 | 12.6494 | 1.1667 | 0.3556 | 8 | 8 | 4 | 3
L8x8 | 0.5625 | 1.1875 | 29.6 | 44.0497 | 2.6667 | 0.8128 |  | L4x3 | 0.3125 | 0.75 | 7.2 | 10.7148 | 1.1667 | 0.3556 | 8 | 8 | 4 | 3
L8x8 | 0.5 | 1.125 | 26.4 | 39.2875 | 2.6667 | 0.8128 |  | L4x3 | 0.25 | 0.6875 | 5.8 | 8.6314 | 1.1667 | 0.3556 | 8 | 8 | 4 | 3
L8x6 | 1 | 1.5 | 44.2 | 65.7769 | 2.3333 | 0.7112 |  | L3 1/2x3 1/2 | 0.5 | 0.875 | 11.1 | 16.5186 | 1.1667 | 0.3556 | 8 | 6 | 3.5 | 3.5
L8x6 | 0.875 | 1.375 | 39.1 | 58.1872 | 2.3333 | 0.7112 |  | L3 1/2x3 1/2 | 0.4375 | 0.8125 | 9.8 | 14.584 | 1.1667 | 0.3556 | 8 | 6 | 3.5 | 3.5
L8x6 | 0.75 | 1.25 | 33.8 | 50.2999 | 2.3333 | 0.7112 |  | L3 1/2x3 1/2 | 0.375 | 0.75 | 8.5 | 12.6494 | 1.1667 | 0.3556 | 8 | 6 | 3.5 | 3.5
L8x6 | 0.625 | 1.125 | 28.5 | 42.4127 | 2.3333 | 0.7112 |  | L3 1/2x3 1/2 | 0.3125 | 0.6875 | 7.2 | 10.7148 | 1.1667 | 0.3556 | 8 | 6 | 3.5 | 3.5
L8x6 | 0.5625 | 1.0625 | 25.7 | 38.2458 | 2.3333 | 0.7112 |  | L3 1/2x3 1/2 | 0.25 | 0.625 | 5.8 | 8.6314 | 1.1667 | 0.3556 | 8 | 6 | 3.5 | 3.5
L8x6 | 0.5 | 1 | 23 | 34.2278 | 2.3333 | 0.7112 | [8 empty] | 8 | 6
L8x6 | 0.4375 | 0.9375 | 20.2 | 30.0609 | 2.3333 | 0.7112 |  | L3 1/2x3 | 0.5 | 0.9375 | 10.2 | 15.1793 | 1.0833 | 0.3302 | 8 | 6 | 3.5 | 3
[8 empty] | L3 1/2x3 | 0.4375 | 0.875 | 9.1 | 13.5423 | 1.0833 | 0.3302 |  |  | 3.5 | 3
L8x4 | 1 | 1.5 | 37.4 | 55.6573 | 2 | 0.6096 |  | L3 1/2x3 | 0.375 | 0.8125 | 7.9 | 11.7565 | 1.0833 | 0.3302 | 8 | 4 | 3.5 | 3
L8x4 | 0.75 | 1.25 | 28.7 | 42.7103 | 2 | 0.6096 |  | L3 1/2x3 | 0.3125 | 0.75 | 6.6 | 9.8219 | 1.0833 | 0.3302 | 8 | 4 | 3.5 | 3
L8x4 | 0.5625 | 1.0625 | 21.9 | 32.5908 | 2 | 0.6096 |  | L3 1/2x3 | 0.25 | 0.6875 | 5.4 | 8.0361 | 1.0833 | 0.3302 | 8 | 4 | 3.5 | 3
L8x4 | 0.5 | 1 | 19.6 | 29.168 | 2 | 0.6096 | [8 empty] | 8 | 4
[8 empty] | L3 1/2x2 1/2 | 0.5 | 0.9375 | 9.4 | 13.9887 | 1 | 0.3048 |  |  | 3.5 | 2.5
L7x4 | 0.75 | 1.25 | 26.2 | 38.9899 | 1.8333 | 0.5588 |  | L3 1/2x2 1/2 | 0.4375 | 0.875 | 8.3 | 12.3518 | 1 | 0.3048 | 7 | 4 | 3.5 | 2.5
L7x4 | 0.625 | 1.125 | 22.1 | 32.8884 | 1.8333 | 0.5588 |  | L3 1/2x2 1/2 | 0.375 | 0.8125 | 7.2 | 10.7148 | 1 | 0.3048 | 7 | 4 | 3.5 | 2.5
L7x4 | 0.5 | 1 | 17.9 | 26.6381 | 1.8333 | 0.5588 |  | L3 1/2x2 1/2 | 0.3125 | 0.75 | 6.1 | 9.0778 | 1 | 0.3048 | 7 | 4 | 3.5 | 2.5
L7x4 | 0.375 | 0.875 | 13.6 | 20.239 | 1.8333 | 0.5588 |  | L3 1/2x2 1/2 | 0.25 | 0.6875 | 4.9 | 7.292 | 1 | 0.3048 | 7 | 4 | 3.5 | 2.5
L6x6 | 1 | 1.5 | 37.4 | 55.6573 | 2 | 0.6096 |  | L3x3 | 0.5 | 0.8125 | 9.4 | 13.9887 | 1 | 0.3048 | 6 | 6 | 3 | 3
L6x6 | 0.875 | 1.375 | 33.1 | 49.2582 | 2 | 0.6096 |  | L3x3 | 0.4375 | 0.75 | 8.3 | 12.3518 | 1 | 0.3048 | 6 | 6 | 3 | 3
L6x6 | 0.75 | 1.25 | 28.7 | 42.7103 | 2 | 0.6096 |  | L3x3 | 0.375 | 0.6875 | 7.2 | 10.7148 | 1 | 0.3048 | 6 | 6 | 3 | 3
L6x6 | 0.625 | 1.125 | 24.2 | 36.0136 | 2 | 0.6096 |  | L3x3 | 0.3125 | 0.625 | 6.1 | 9.0778 | 1 | 0.3048 | 6 | 6 | 3 | 3
L6x6 | 0.5625 | 1.0625 | 21.9 | 32.5908 | 2 | 0.6096 |  | L3x3 | 0.25 | 0.5625 | 4.9 | 7.292 | 1 | 0.3048 | 6 | 6 | 3 | 3
L6x6 | 0.5 | 1 | 19.6 | 29.168 | 2 | 0.6096 |  | L3x3 | 0.1875 | 0.5 | 3.71 | 5.5211 | 1 | 0.3048 | 6 | 6 | 3 | 3
L6x6 | 0.4375 | 0.9375 | 17.2 | 25.5964 | 2 | 0.6096 | [8 empty] | 6 | 6
L6x6 | 0.375 | 0.875 | 14.9 | 22.1736 | 2 | 0.6096 |  | L3x2 1/2 | 0.5 | 0.875 | 8.5 | 12.6494 | 0.91667 | 0.2794 | 6 | 6 | 3 | 2.5
L6x6 | 0.3125 | 0.8125 | 12.4 | 18.4532 | 2 | 0.6096 |  | L3x2 1/2 | 0.4375 | 0.8125 | 7.6 | 11.31 | 0.91667 | 0.2794 | 6 | 6 | 3 | 2.5
[8 empty] | L3x2 1/2 | 0.375 | 0.75 | 6.6 | 9.8219 | 0.91667 | 0.2794 |  |  | 3 | 2.5
L6x4 | 0.875 | 1.375 | 27.2 | 40.4781 | 1.6667 | 0.508 |  | L3x2 1/2 | 0.3125 | 0.6875 | 5.6 | 8.3337 | 0.91667 | 0.2794 | 6 | 4 | 3 | 2.5
L6x4 | 0.75 | 1.25 | 23.6 | 35.1207 | 1.6667 | 0.508 |  | L3x2 1/2 | 0.25 | 0.625 | 4.5 | 6.6967 | 0.91667 | 0.2794 | 6 | 4 | 3 | 2.5
L6x4 | 0.625 | 1.125 | 20 | 29.7633 | 1.6667 | 0.508 |  | L3x2 1/2 | 0.1875 | 0.5625 | 3.39 | 5.0449 | 0.91667 | 0.2794 | 6 | 4 | 3 | 2.5
L6x4 | 0.5625 | 1.0625 | 18.1 | 26.9358 | 1.6667 | 0.508 | [8 empty] | 6 | 4
L6x4 | 0.5 | 1 | 16.2 | 24.1083 | 1.6667 | 0.508 |  | L3x2 | 0.5 | 0.8125 | 7.7 | 11.4589 | 0.83333 | 0.254 | 6 | 4 | 3 | 2
L6x4 | 0.4375 | 0.9375 | 14.3 | 21.2807 | 1.6667 | 0.508 |  | L3x2 | 0.4375 | 0.75 | 6.8 | 10.1195 | 0.83333 | 0.254 | 6 | 4 | 3 | 2
L6x4 | 0.375 | 0.875 | 12.3 | 18.3044 | 1.6667 | 0.508 |  | L3x2 | 0.375 | 0.6875 | 5.9 | 8.7802 | 0.83333 | 0.254 | 6 | 4 | 3 | 2
L6x4 | 0.3125 | 0.8125 | 10.3 | 15.3281 | 1.6667 | 0.508 |  | L3x2 | 0.3125 | 0.625 | 5 | 7.4408 | 0.83333 | 0.254 | 6 | 4 | 3 | 2
[8 empty] | L3x2 | 0.25 | 0.5625 | 4.1 | 6.1015 | 0.83333 | 0.254 |  |  | 3 | 2
L6x3 1/2 | 0.5 | 1 | 15.3 | 22.7689 | 1.5833 | 0.4826 |  | L3x2 | 0.1875 | 0.5 | 3.07 | 4.5687 | 0.83333 | 0.254 | 6 | 3.5 | 3 | 2
L6x3 1/2 | 0.375 | 0.875 | 11.7 | 17.4115 | 1.5833 | 0.4826 | [8 empty] | 6 | 3.5
L6x3 1/2 | 0.3125 | 0.8125 | 9.8 | 14.584 | 1.5833 | 0.4826 |  | L2 1/2x2 1/2 | 0.5 | 0.8125 | 7.7 | 11.4589 | 0.83333 | 0.254 | 6 | 3.5 | 2.5 | 2.5
[8 empty] | L2 1/2x2 1/2 | 0.375 | 0.6875 | 5.9 | 8.7802 | 0.83333 | 0.254 |  |  | 2.5 | 2.5
L5x5 | 0.875 | 1.375 | 27.2 | 40.4781 | 1.6667 | 0.508 |  | L2 1/2x2 1/2 | 0.3125 | 0.625 | 5 | 7.4408 | 0.83333 | 0.254 | 5 | 5 | 2.5 | 2.5
L5x5 | 0.75 | 1.25 | 23.6 | 35.1207 | 1.6667 | 0.508 |  | L2 1/2x2 1/2 | 0.25 | 0.5625 | 4.1 | 6.1015 | 0.83333 | 0.254 | 5 | 5 | 2.5 | 2.5
L5x5 | 0.625 | 1.125 | 20 | 29.7633 | 1.6667 | 0.508 |  | L2 1/2x2 1/2 | 0.1875 | 0.5 | 3.07 | 4.5687 | 0.83333 | 0.254 | 5 | 5 | 2.5 | 2.5
L5x5 | 0.5 | 1 | 16.2 | 24.1083 | 1.6667 | 0.508 | [8 empty] | 5 | 5
L5x5 | 0.4375 | 0.9375 | 14.3 | 21.2807 | 1.6667 | 0.508 |  | L2 1/2x2 | 0.375 | 0.6875 | 5.3 | 7.8873 | 0.75 | 0.2286 | 5 | 5 | 2.5 | 2
L5x5 | 0.375 | 0.875 | 12.3 | 18.3044 | 1.6667 | 0.508 |  | L2 1/2x2 | 0.3125 | 0.625 | 4.5 | 6.6967 | 0.75 | 0.2286 | 5 | 5 | 2.5 | 2
L5x5 | 0.3125 | 0.8125 | 10.3 | 15.3281 | 1.6667 | 0.508 |  | L2 1/2x2 | 0.25 | 0.5625 | 3.62 | 5.3872 | 0.75 | 0.2286 | 5 | 5 | 2.5 | 2
[8 empty] | L2 1/2x2 | 0.1875 | 0.5 | 2.75 | 4.0925 | 0.75 | 0.2286 |  |  | 2.5 | 2
L5x3 1/2 | 0.75 | 1.25 | 19.8 | 29.4656 | 1.4167 | 0.4318 | [8 empty] | 5 | 3.5
L5x3 1/2 | 0.625 | 1.125 | 16.8 | 25.0012 | 1.4167 | 0.4318 |  | L2x2 | 0.375 | 0.625 | 4.7 | 6.9944 | 0.66667 | 0.2032 | 5 | 3.5 | 2 | 2
L5x3 1/2 | 0.5 | 1 | 13.6 | 20.239 | 1.4167 | 0.4318 |  | L2x2 | 0.3125 | 0.5625 | 3.92 | 5.8336 | 0.66667 | 0.2032 | 5 | 3.5 | 2 | 2
L5x3 1/2 | 0.4375 | 0.9375 | 12 | 17.858 | 1.4167 | 0.4318 |  | L2x2 | 0.25 | 0.5 | 3.19 | 4.7472 | 0.66667 | 0.2032 | 5 | 3.5 | 2 | 2
L5x3 1/2 | 0.375 | 0.875 | 10.4 | 15.4769 | 1.4167 | 0.4318 |  | L2x2 | 0.1875 | 0.4375 | 2.44 | 3.6311 | 0.66667 | 0.2032 | 5 | 3.5 | 2 | 2
L5x3 1/2 | 0.3125 | 0.8125 | 8.7 | 12.947 | 1.4167 | 0.4318 |  | L2x2 | 0.125 | 0.375 | 1.65 | 2.4555 | 0.66667 | 0.2032 | 5 | 3.5 | 2 | 2
L5x3 1/2 | 0.25 | 0.75 | 7 | 10.4171 | 1.4167 | 0.4318 | [8 empty] | 5 | 3.5
[8 empty] | L1 3/4x1 3/4 | 0.25 | 0.5 | 2.77 | 4.1222 | 0.58333 | 0.1778 |  |  | 1.75 | 1.75
L5x3 | 0.625 | 1 | 15.7 | 23.3642 | 1.3333 | 0.4064 |  | L1 3/4x1 3/4 | 0.1875 | 0.4375 | 2.12 | 3.1549 | 0.58333 | 0.1778 | 5 | 3 | 1.75 | 1.75
L5x3 | 0.5 | 1 | 12.8 | 19.0485 | 1.3333 | 0.4064 | [8 empty] | 5 | 3
L5x3 | 0.4375 | 0.9375 | 11.3 | 16.8163 | 1.3333 | 0.4064 |  | L1 1/2x1 1/2 | 0.25 | 0.4375 | 2.34 | 3.4823 | 0.5 | 0.1524 | 5 | 3 | 1.5 | 1.5
L5x3 | 0.375 | 0.875 | 9.8 | 14.584 | 1.3333 | 0.4064 |  | L1 1/2x1 1/2 | 0.1875 | 0.375 | 1.8 | 2.6787 | 0.5 | 0.1524 | 5 | 3 | 1.5 | 1.5
L5x3 | 0.3125 | 0.8125 | 8.2 | 12.2029 | 1.3333 | 0.4064 | [8 empty] | 5 | 3
L5x3 | 0.25 | 0.75 | 6.6 | 9.8219 | 1.3333 | 0.4064 |  | L1 1/4x1 1/4 | 0.25 | 0.4375 | 1.92 | 2.8573 | 0.41667 | 0.127 | 5 | 3 | 1.25 | 1.25
[8 empty] | L1 1/4x1 1/4 | 0.1875 | 0.375 | 1.48 | 2.2025 | 0.41667 | 0.127 |  |  | 1.25 | 1.25
L4x4 | 0.75 | 1.125 | 18.5 | 27.531 | 1.3333 | 0.4064 | [8 empty] | 4 | 4
L4x4 | 0.625 | 1 | 15.7 | 23.3642 | 1.3333 | 0.4064 |  | L1 1/8x1 1/8 | 0.125 | 0.21875 | 0.9 | 1.3393 | 0.375 | 0.1143 | 4 | 4 | 1.125 | 1.125
L4x4 | 0.5 | 0.875 | 12.8 | 19.0485 | 1.3333 | 0.4064 | [8 empty] | 4 | 4
L4x4 | 0.4375 | 0.8125 | 11.3 | 16.8163 | 1.3333 | 0.4064 |  | L1x1 | 0.125 | 0.25 | 0.8 | 1.1905 | 0.33333 | 0.1016 | 4 | 4 | 1 | 1
L4x4 | 0.375 | 0.75 | 9.8 | 14.584 | 1.3333 | 0.4064 | [8 empty] | 4 | 4 | 1 | 1
L4x4 | 0.3125 | 0.6875 | 8.2 | 12.2029 | 1.3333 | 0.4064 | [8 empty] | 4 | 4
L4x4 | 0.25 | 0.625 | 6.6 | 9.8219 | 1.3333 | 0.4064 | [8 empty] | 4 | 4

## W Tees
2017-06-13 14:31
Flg. Width "bf"
Flg Gage
k1
|  | Flg. Thk "tf" | [5 empty] | k
Web Gage
Structutral Tees |  |  | Depth
Cut from W shapes |  |  | "d" |  |  | Stem Thk. "tw"
WTee | Depth | Stem Thk. | Flg. Width | Flg. Thk. | k | k1 | Flange | Web | Sq. Ft.- Surf | Sq.M.- Surf | Weight
Size | d | tw | bf | tf |  |  | Bolt Gage | Bolt Gage | Area - per Ft | Area - per M | Kg per M
WT18x179.5 | 18.6875 | 1.125 | 16.75 | 2 | 3.125 |  |  |  | 5.9062 | 1.8002 | 267.1254 | 179.5
WT18x164 | 18.5625 | 1 | 16.625 | 1.875 | 3 |  |  |  | 5.8646 | 1.7875 | 244.0589 | 164
WT18x150 | 18.375 | 0.9375 | 16.625 | 1.6875 | 2.8125 | 1.5 | 5.5 | 3.75 | 5.8333 | 1.778 | 223.2246 | 150
WT18x140 | 18.25 | 0.875 | 16.625 | 1.5625 | 2.6875 | 1.5 | 5.5 | 3.75 | 5.8125 | 1.7717 | 208.343 | 140
WT18x130 | 18.125 | 0.8125 | 16.5 | 1.4375 | 2.5625 | 1.5 | 5.5 | 3.5 | 5.7708 | 1.759 | 193.4613 | 130
WT18x122.5 | 18 | 0.8125 | 16.5 | 1.375 | 2.5 | 1.4375 | 5.5 | 3.5 | 5.75 | 1.7526 | 182.3001 | 122.5
WT18x115 | 18 | 0.75 | 16.5 | 1.25 | 2.375 | 1.4375 | 5.5 | 3.5 | 5.75 | 1.7526 | 171.1389 | 115
WT18x128 | 18.6875 | 1 | 12.25 | 1.75 | 2.625 |  |  |  | 5.1562 | 1.5716 | 190.485 | 128
WT18x116 | 18.5625 | 0.875 | 12.125 | 1.5625 | 2.5 |  |  |  | 5.1146 | 1.5589 | 172.627 | 116
WT18x105 | 18.375 | 0.8125 | 12.125 | 1.375 | 2.3125 | 1.25 | 5.5 | 3.5 | 5.0833 | 1.5494 | 156.2572 | 105
WT18x97 | 18.25 | 0.75 | 12.125 | 1.25 | 2.1875 | 1.1875 | 5.5 | 3.5 | 5.0625 | 1.5431 | 144.3519 | 97
WT18x91 | 18.125 | 0.75 | 12.125 | 1.1875 | 2.125 | 1.1875 | 5.5 | 3.25 | 5.0417 | 1.5367 | 135.4229 | 91
WT18x85 | 18.125 | 0.6875 | 12 | 1.125 | 2 | 1.1875 | 5.5 | 3.25 | 5.0208 | 1.5304 | 126.4939 | 85
WT18x80 | 18 | 0.625 | 12 | 1 | 1.9375 | 1.125 | 5.5 | 3.25 | 5 | 1.524 | 119.0531 | 80
WT18x75 | 17.875 | 0.625 | 12 | 0.9375 | 1.875 | 1.125 | 5.5 | 3 | 4.9792 | 1.5177 | 111.6123 | 75
WT18x67.5 | 17.75 | 0.625 | 12 | 0.8125 | 1.6875 | 1.125 | 5.5 | 3 | 4.9583 | 1.5113 | 100.4511 | 67.5
WT16.5x177 | 17.75 | 1.1875 | 16.125 | 2.0625 | 2.875 |  |  |  | 5.6458 | 1.7209 | 263.405 | 177
WT16.5x159 | 17.5625 | 1.0625 | 16 | 1.875 | 2.6875 |  |  |  | 5.5938 | 1.705 | 236.6181 | 159
WT16.5x145.5 | 17.4375 | 1 | 15.875 | 1.75 | 2.5625 |  |  |  | 5.5521 | 1.6923 | 216.5279 | 145.5
WT16.5x131.5 | 17.25 | 0.875 | 15.75 | 1.5625 | 2.375 |  |  |  | 5.5 | 1.6764 | 195.6936 | 131.5
WT16.5x120.5 | 17.125 | 0.8125 | 15.875 | 1.375 | 2.1875 | 1.25 | 5.5 | 3.5 | 5.5 | 1.6764 | 179.3238 | 120.5
WT16.5x110.5 | 17 | 0.75 | 15.75 | 1.25 | 2.0625 | 1.1875 | 5.5 | 3.5 | 5.4583 | 1.6637 | 164.4421 | 110.5
WT16.5x100.5 | 16.875 | 0.6875 | 15.75 | 1.125 | 1.9375 | 1.125 | 5.5 | 3.25 | 5.4375 | 1.6574 | 149.5605 | 100.5
WT16.5x84.5 | 16.9375 | 0.6875 | 11.5 | 1.25 | 2.0625 |  |  |  | 4.7396 | 1.4446 | 125.7499 | 84.5
WT16.5x76 | 16.75 | 0.625 | 11.625 | 1.0625 | 1.875 | 1.125 | 5.5 | 3.25 | 4.7292 | 1.4415 | 113.1005 | 76
WT16.5x70.5 | 16.625 | 0.625 | 11.5 | 0.9375 | 1.75 | 1.0625 | 5.5 | 3 | 4.6875 | 1.4288 | 104.9156 | 70.5
WT16.5x65 | 16.5 | 0.5625 | 11.5 | 0.875 | 1.6875 | 1.0625 | 5.5 | 3 | 4.6667 | 1.4224 | 96.7307 | 65
WT16.5x59 | 16.375 | 0.5625 | 11.5 | 0.75 | 1.5625 | 1.0625 | 5.5 | 2.75 | 4.6458 | 1.4161 | 87.8017 | 59
WT15x117.5 | 15.625 | 0.8125 | 15 | 1.5 | 2.25 |  |  |  | 5.1042 | 1.5558 | 174.8593 | 117.5
WT15x105.5 | 15.5 | 0.75 | 15.125 | 1.3125 | 2.125 | 1.125 | 5.5 | 3.5 | 5.1042 | 1.5558 | 157.0013 | 105.5
WT15x95.5 | 15.375 | 0.6875 | 15 | 1.1875 | 1.9375 | 1.0625 | 5.5 | 3.25 | 5.0625 | 1.5431 | 142.1197 | 95.5
WT15x86.5 | 15.25 | 0.625 | 15 | 1.0625 | 1.875 | 1.0625 | 5.5 | 3.25 | 5.0417 | 1.5367 | 128.7262 | 86.5
WT15x74 | 15.3125 | 0.625 | 10.5 | 1.1875 | 2 |  |  |  | 4.3021 | 1.3113 | 110.1241 | 74
WT15x66 | 15.125 | 0.625 | 10.5 | 1 | 1.75 | 1.0625 | 5.5 | 3 | 4.2708 | 1.3018 | 98.2188 | 66
WT15x62 | 15.125 | 0.5625 | 10.5 | 0.9375 | 1.6875 | 1 | 5.5 | 3 | 4.2708 | 1.3018 | 92.2662 | 62
WT15x58 | 15 | 0.5625 | 10.5 | 0.875 | 1.625 | 1 | 5.5 | 3 | 4.25 | 1.2954 | 86.3135 | 58
WT15x54 | 14.875 | 0.5625 | 10.5 | 0.75 | 1.5625 | 1 | 5.5 | 3 | 4.2292 | 1.2891 | 80.3609 | 54
WT15x49.5 | 14.875 | 0.5 | 10.5 | 0.6875 | 1.4375 | 1 | 5.5 | 2.75 | 4.2292 | 1.2891 | 73.6641 | 49.5
WT13.5x108.5 | 14.1875 | 0.8125 | 14.125 | 1.5 | 2.1875 |  |  |  | 4.7188 | 1.4383 | 161.4658 | 108.5
WT13.5X97 | 14.0625 | 0.75 | 14 | 1.3125 | 2.0625 |  |  |  | 4.6771 | 1.4256 | 144.3519 | 97
WT13.5x89 | 13.875 | 0.75 | 14.125 | 1.1875 | 1.875 | 1.0625 | 5.5 | 3.25 | 4.6667 | 1.4224 | 132.4466 | 89
WT13.5x80.5 | 13.75 | 0.6875 | 14 | 1.0625 | 1.8125 | 1 | 5.5 | 3.25 | 4.625 | 1.4097 | 119.7972 | 80.5
WT13.5x73 | 13.75 | 0.625 | 14 | 1 | 1.6875 | 1 | 5.5 | 3 | 4.625 | 1.4097 | 108.636 | 73
Wt13.5x64.5 | 13.8125 | 0.625 | 10 | 1.125 | 1.8125 |  |  |  | 3.9688 | 1.2097 | 95.9866 | 64.5
WT13.5x57 | 13.625 | 0.5625 | 10.125 | 0.9375 | 1.625 | 0.9375 | 5.5 | 3 | 3.9583 | 1.2065 | 84.8254 | 57
WT13.5x51 | 13.5 | 0.5 | 10 | 0.8125 | 1.5625 | 0.9375 | 5.5 | 3 | 3.9167 | 1.1938 | 75.8964 | 51
WT13.5x47 | 13.5 | 0.5 | 10 | 0.75 | 1.4375 | 0.9375 | 5.5 | 2.75 | 3.9167 | 1.1938 | 69.9437 | 47
WT13.5x42 | 13.375 | 0.4375 | 10 | 0.625 | 1.375 | 0.9375 | 5.5 | 2.75 | 3.8958 | 1.1875 | 62.5029 | 42
WT12x88 | 12.625 | 0.75 | 12.875 | 1.3125 | 2.125 |  |  |  | 4.25 | 1.2954 | 130.9584 | 88
WT12x81 | 12.5 | 0.6875 | 13 | 1.25 | 2 | 1.0625 | 5.5 | 3.25 | 4.25 | 1.2954 | 120.5413 | 81
WT12x73 | 12.375 | 0.625 | 12.875 | 1.0625 | 1.875 | 1.0625 | 5.5 | 3.25 | 4.2083 | 1.2827 | 108.636 | 73
WT12x65.5 | 12.25 | 0.625 | 12.875 | 0.9375 | 1.75 | 1.0625 | 5.5 | 3 | 4.1875 | 1.2764 | 97.4747 | 65.5
WT12x58.5 | 12.125 | 0.5625 | 12.75 | 0.875 | 1.625 | 1 | 5.5 | 3 | 4.1458 | 1.2637 | 87.0576 | 58.5
WT12x52 | 12 | 0.5 | 12.75 | 0.75 | 1.5 | 1 | 5.5 | 2.75 | 4.125 | 1.2573 | 77.3845 | 52
WT12x51.5 | 12.25 | 0.5625 | 9 | 1 | 1.75 |  |  |  | 3.5417 | 1.0795 | 76.6404 | 51.5
WT12x47 | 12.125 | 0.5 | 9.125 | 0.875 | 1.625 | 1 | 5.5 | 3 | 3.5417 | 1.0795 | 69.9437 | 47
WT12x42 | 12 | 0.5 | 9 | 0.75 | 1.5625 | 0.9375 | 5.5 | 3 | 3.5 | 1.0668 | 62.5029 | 42
WT12x38 | 12 | 0.4375 | 9 | 0.6875 | 1.4375 | 0.9375 | 5.5 | 2.75 | 3.5 | 1.0668 | 56.5502 | 38
WT12x34 | 11.875 | 0.4375 | 9 | 0.5625 | 1.375 | 0.9375 | 5.5 | 2.75 | 3.4792 | 1.0605 | 50.5976 | 34
WT12x31 | 11.875 | 0.4375 | 7 | 0.5625 | 1.375 | 0.9375 | 3.5 | 2.75 | 3.1458 | 0.95885 | 46.1331 | 31
WT12x27.5 | 11.75 | 0.375 | 7 | 0.5 | 1.3125 | 0.9375 | 3.5 | 2.75 | 3.125 | 0.9525 | 40.9245 | 27.5
WT10.5x83 | 11.25 | 0.75 | 12.375 | 1.375 | 2.125 |  |  |  | 3.9375 | 1.2002 | 123.5176 | 83
WT10.5x73.5 | 11 | 0.75 | 12.5 | 1.125 | 1.875 | 1.0625 | 5.5 | 3.25 | 3.9167 | 1.1938 | 109.3801 | 73.5
WT10.5x66 | 10.875 | 0.625 | 12.5 | 1.0625 | 1.8125 | 1 | 5.5 | 3 | 3.8958 | 1.1875 | 98.2188 | 66
WT10.5x61 | 10.875 | 0.625 | 12.375 | 0.9375 | 1.6875 | 1 | 5.5 | 3 | 3.875 | 1.1811 | 90.778 | 61
WT10.5x55.5 | 10.75 | 0.5625 | 12.375 | 0.875 | 1.625 | 0.9375 | 5.5 | 2.75 | 3.8542 | 1.1748 | 82.5931 | 55.5
WT10.5x50.5 | 10.625 | 0.5 | 12.25 | 0.8125 | 1.5625 | 0.9375 | 5.5 | 2.75 | 3.8125 | 1.1621 | 75.1523 | 50.5
WT10.5x46.5 | 10.75 | 0.5625 | 8.375 | 0.9375 | 1.6875 | 1 | 5.5 | 3 | 3.1875 | 0.97155 | 69.1996 | 46.5
WT10.5x41.5 | 10.75 | 0.5 | 8.375 | 0.8125 | 1.5625 | 0.9375 | 5.5 | 2.75 | 3.1875 | 0.97155 | 61.7588 | 41.5
WT10.5x36.5 | 10.625 | 0.4375 | 8.25 | 0.75 | 1.5 | 0.9375 | 5.5 | 2.75 | 3.1458 | 0.95885 | 54.318 | 36.5
WT10.5x34 | 10.625 | 0.4375 | 8.25 | 0.6875 | 1.4375 | 0.875 | 5.5 | 2.75 | 3.1458 | 0.95885 | 50.5976 | 34
WT10.5x31 | 10.5 | 0.375 | 8.25 | 0.625 | 1.375 | 0.875 | 5.5 | 2.5 | 3.125 | 0.9525 | 46.1331 | 31
WT10.5x28.5 | 10.5 | 0.375 | 6.5 | 0.625 | 1.375 | 0.875 | 3.5 | 2.75 | 2.8333 | 0.8636 | 42.4127 | 28.5
WT10.5x25 | 10.375 | 0.375 | 6.5 | 0.5625 | 1.3125 | 0.875 | 3.5 | 2.5 | 2.8125 | 0.85725 | 37.2041 | 25
WT10.5x22 | 10.375 | 0.375 | 6.5 | 0.4375 | 1.1875 | 0.875 | 3.5 | 2.5 | 2.8125 | 0.85725 | 32.7396 | 22
WT9x71.5 | 9.75 | 0.75 | 11.25 | 1.3125 | 2 |  |  |  | 3.5 | 1.0668 | 106.4037 | 71.5
WT9x65 | 9.625 | 0.6875 | 11.125 | 1.1875 | 1.875 |  |  |  | 3.4583 | 1.0541 | 96.7307 | 65
WT9x59.5 | 9.5 | 0.625 | 11.25 | 1.0625 | 1.75 | 0.9375 | 5.5 | 3 | 3.4583 | 1.0541 | 88.5458 | 59.5
WT9x53 | 9.375 | 0.5625 | 11.25 | 0.9375 | 1.625 | 0.9375 | 5.5 | 3 | 3.4375 | 1.0478 | 78.8727 | 53
WT9x48.5 | 9.25 | 0.5625 | 11.125 | 0.875 | 1.5625 | 0.875 | 5.5 | 2.75 | 3.3958 | 1.0351 | 72.176 | 48.5
WT9x43 | 9.25 | 0.5 | 11.125 | 0.75 | 1.4375 | 0.875 | 5.5 | 2.75 | 3.3958 | 1.0351 | 63.9911 | 43
WT9x38 | 9.125 | 0.4375 | 11 | 0.6875 | 1.375 | 0.8125 | 5.5 | 2.75 | 3.3542 | 1.0224 | 56.5502 | 38
WT9x35.5 | 9.25 | 0.5 | 7.625 | 0.8125 | 1.5 | 0.875 | 3.5 | 2.75 | 2.8125 | 0.85725 | 52.8298 | 35.5
WT9x32.5 | 9.125 | 0.4375 | 7.625 | 0.75 | 1.4375 | 0.875 | 3.5 | 2.75 | 2.7917 | 0.8509 | 48.3653 | 32.5
WT9x30 | 9.125 | 0.4375 | 7.5 | 0.6875 | 1.375 | 0.8125 | 3.5 | 2.75 | 2.7708 | 0.84455 | 44.6449 | 30
WT9x27.5 | 9 | 0.375 | 7.5 | 0.625 | 1.3125 | 0.8125 | 3.5 | 2.75 | 2.75 | 0.8382 | 40.9245 | 27.5
WT9x25 | 9 | 0.375 | 7.5 | 0.5625 | 1.25 | 0.8125 | 3.5 | 2.5 | 2.75 | 0.8382 | 37.2041 | 25
WT9x23 | 9 | 0.375 | 6 | 0.625 | 1.25 | 0.8125 | 3.5 | 2.5 | 2.5 | 0.762 | 34.2278 | 23
WT9x20 | 9 | 0.3125 | 6 | 0.5 | 1.1875 | 0.8125 | 3.5 | 2.5 | 2.5 | 0.762 | 29.7633 | 20
WT9x17.5 | 8.875 | 0.3125 | 6 | 0.4375 | 1.125 | 0.75 | 3.5 | 2.5 | 2.4792 | 0.75565 | 26.0429 | 17.5
WT8x50 | 8.5 | 0.5625 | 10.375 | 1 | 1.6875 | 0.9375 | 5.5 | 3 | 3.1458 | 0.95885 | 74.4082 | 50
WT8x44.5 | 8.375 | 0.5 | 10.375 | 0.875 | 1.5625 | 0.875 | 5.5 | 2.75 | 3.125 | 0.9525 | 66.2233 | 44.5
WT8x38.5 | 8.25 | 0.4375 | 10.25 | 0.75 | 1.4375 | 0.875 | 5.5 | 2.75 | 3.0833 | 0.9398 | 57.2943 | 38.5
WT8x33.5 | 8.125 | 0.375 | 10.25 | 0.6875 | 1.375 | 0.8125 | 5.5 | 2.75 | 3.0625 | 0.93345 | 49.8535 | 33.5
WT8x28.5 | 8.25 | 0.4375 | 7.125 | 0.6875 | 1.375 | 0.875 | 3.5 | 2.75 | 2.5625 | 0.78105 | 42.4127 | 28.5
WT8x25 | 8.125 | 0.375 | 7.125 | 0.625 | 1.3125 | 0.8125 | 3.5 | 2.75 | 2.5417 | 0.7747 | 37.2041 | 25
WT8x22.5 | 8.125 | 0.375 | 7 | 0.5625 | 1.25 | 0.8125 | 3.5 | 2.5 | 2.5208 | 0.76835 | 33.4837 | 22.5
WT8x20 | 8 | 0.3125 | 7 | 0.5 | 1.1875 | 0.8125 | 3.5 | 2.5 | 2.5 | 0.762 | 29.7633 | 20
WT8x18 | 7.875 | 0.3125 | 7 | 0.4375 | 1.125 | 0.75 | 3.5 | 2.5 | 2.4792 | 0.75565 | 26.787 | 18
WT8x15.5 | 8 | 0.25 | 5.5 | 0.4375 | 1.125 | 0.75 | 2.75 | 2.5 | 2.25 | 0.6858 | 23.0665 | 15.5
WT8x13 | 7.875 | 0.25 | 5.5 | 0.375 | 1.0625 | 0.75 | 2.75 | 2.25 | 2.2292 | 0.67945 | 19.3461 | 13
WT7x365 | 11.25 | 3.0625 | 17.875 | 4.9375 | 5.5625 | 2.1875 | na | na | 4.8542 | 1.4796 | 543.1799 | 365
WT7x332.5 | 10.875 | 2.8125 | 17.625 | 4.5 | 5.1875 | 2.0625 | na | na | 4.75 | 1.4478 | 494.8145 | 332.5
WT7x302.5 | 10.5 | 2.625 | 17.375 | 4.1875 | 4.8125 | 1.9375 | na | na | 4.6458 | 1.4161 | 450.1696 | 302.5
WT7x275 | 10.125 | 2.375 | 17.25 | 3.8125 | 4.5 | 1.8125 | na | na | 4.5625 | 1.3907 | 409.2451 | 275
WT7x250 | 9.75 | 2.1875 | 17 | 3.5 | 4.1875 | 1.75 | na | na | 4.4583 | 1.3589 | 372.041 | 250
WT7x227.5 | 9.5 | 2 | 16.875 | 3.1875 | 3.875 | 1.625 | na | na | 4.3958 | 1.3399 | 338.5573 | 227.5
WT7x213 | 9.375 | 1.875 | 16.75 | 3.0625 | 3.6875 | 1.5625 | na | na | 4.3542 | 1.3272 | 316.9789 | 213
WT7x199 | 9.125 | 1.75 | 16.625 | 2.875 | 3.5 | 1.5 | na | na | 4.2917 | 1.3081 | 296.1446 | 199
WT7x185 | 9 | 1.625 | 16.5 | 2.6875 | 3.3125 | 1.4375 | na | na | 4.25 | 1.2954 | 275.3103 | 185
WT7x171 | 8.75 | 1.5625 | 16.375 | 2.5 | 3.125 | 1.375 | na | na | 4.1875 | 1.2764 | 254.4761 | 171
WT7x155.5 | 8.5 | 1.4375 | 16.25 | 2.25 | 2.9375 | 1.3125 | na | na | 4.125 | 1.2573 | 231.4095 | 155.5
WT7x141.5 | 8.375 | 1.3125 | 16.125 | 2.0625 | 2.75 | 1.25 | na | na | 4.0833 | 1.2446 | 210.5752 | 141.5
WT7x128.5 | 8.25 | 1.1875 | 16 | 1.875 | 2.5625 | 1.1875 | na | na | 4.0417 | 1.2319 | 191.2291 | 128.5
WT7x116.5 | 8 | 1.0625 | 15.875 | 1.75 | 2.375 | 1.1875 | na | na | 3.9792 | 1.2129 | 173.3711 | 116.5
WT7x105.5 | 7.875 | 1 | 15.75 | 1.5625 | 2.25 | 1.125 | na | na | 3.9375 | 1.2002 | 157.0013 | 105.5
WT7x96.5 | 7.75 | 0.875 | 15.75 | 1.4375 | 2.125 | 1.0625 | na | na | 3.9167 | 1.1938 | 143.6078 | 96.5
WT7x88 | 7.625 | 0.8125 | 15.625 | 1.3125 | 2 | 1.0625 | na | na | 3.875 | 1.1811 | 130.9584 | 88
WT7x79.5 | 7.5 | 0.75 | 15.625 | 1.1875 | 1.875 | 1 | na | na | 3.8542 | 1.1748 | 118.309 | 79.5
WT7x72.5 | 7.375 | 0.6875 | 15.5 | 1.0625 | 1.75 | 1 | na | na | 3.8125 | 1.1621 | 107.8919 | 72.5
WT7x66 | 7.375 | 0.625 | 14.75 | 1 | 1.6875 | 0.9375 | 5.5 | 3 | 3.6875 | 1.124 | 98.2188 | 66
WT7x60 | 7.25 | 0.5625 | 14.625 | 0.9375 | 1.625 | 0.9375 | 5.5 | 3 | 3.6458 | 1.1113 | 89.2898 | 60
WT7x54.5 | 7.125 | 0.5 | 14.625 | 0.875 | 1.5625 | 0.875 | 5.5 | 2.75 | 3.625 | 1.1049 | 81.1049 | 54.5
WT7x49.5 | 7.125 | 0.5 | 14.625 | 0.75 | 1.4375 | 0.875 | 5.5 | 2.75 | 3.625 | 1.1049 | 73.6641 | 49.5
WT7x45 | 7 | 0.4375 | 14.5 | 0.6875 | 1.375 | 0.875 | 5.5 | 2.75 | 3.5833 | 1.0922 | 66.9674 | 45
WT7x41 | 7.125 | 0.5 | 10.125 | 0.875 | 1.625 | 1 | 5.5 | 2.75 | 2.875 | 0.8763 | 61.0147 | 41
WT7x37 | 7.125 | 0.4375 | 10.125 | 0.8125 | 1.5625 | 0.9375 | 5.5 | 2.75 | 2.875 | 0.8763 | 55.0621 | 37
WT7x34 | 7 | 0.4375 | 10 | 0.75 | 1.5 | 0.9375 | 5.5 | 2.75 | 2.8333 | 0.8636 | 50.5976 | 34
WT7x30.5 | 7 | 0.375 | 10 | 0.625 | 1.4375 | 0.9375 | 5.5 | 2.75 | 2.8333 | 0.8636 | 45.389 | 30.5
WT7x26.5 | 7 | 0.375 | 8 | 0.6875 | 1.4375 | 0.9375 | 5.5 | 2.75 | 2.5 | 0.762 | 39.4363 | 26.5
WT7x24 | 6.875 | 0.3125 | 8 | 0.625 | 1.375 | 0.875 | 5.5 | 2.5 | 2.4792 | 0.75565 | 35.7159 | 24
WT7x21.5 | 6.875 | 0.3125 | 8 | 0.5 | 1.3125 | 0.875 | 5.5 | 2.5 | 2.4792 | 0.75565 | 31.9955 | 21.5
WT7x19 | 7 | 0.3125 | 6.75 | 0.5 | 1.0625 | 0.625 | 3.5 | 2.5 | 2.2917 | 0.6985 | 28.2751 | 19
WT7x17 | 7 | 0.3125 | 6.75 | 0.4375 | 1 | 0.625 | 3.5 | 2.5 | 2.2917 | 0.6985 | 25.2988 | 17
WT7x15 | 6.875 | 0.25 | 6.75 | 0.375 | 0.9375 | 0.625 | 3.5 | 2.5 | 2.2708 | 0.69215 | 22.3225 | 15
WT7x13 | 7 | 0.25 | 5 | 0.4375 | 0.9375 | 0.5625 | 2.75 | 2.5 | 2 | 0.6096 | 19.3461 | 13
WT7x11 | 6.875 | 0.25 | 5 | 0.3125 | 0.875 | 0.5625 | 2.75 | 2.25 | 1.9792 | 0.60325 | 16.3698 | 11
WT6x168 | 8.375 | 1.75 | 13.375 | 2.9375 | 3.6875 | 1.5 | na | na | 3.625 | 1.1049 | 250.0116 | 168
WT6x152.5 | 8.125 | 1.625 | 13.25 | 2.6875 | 3.4375 | 1.4375 | na | na | 3.5625 | 1.0859 | 226.945 | 152.5
WT6x139.5 | 7.875 | 1.5 | 13.125 | 2.5 | 3.1875 | 1.375 | na | na | 3.5 | 1.0668 | 207.5989 | 139.5
WT6x126 | 7.75 | 1.375 | 13 | 2.25 | 2.9375 | 1.3125 | na | na | 3.4583 | 1.0541 | 187.5087 | 126
WT6x115 | 7.5 | 1.3125 | 12.875 | 2.0625 | 2.75 | 1.25 | na | na | 3.3958 | 1.0351 | 171.1389 | 115
WT6x105 | 7.375 | 1.1875 | 12.75 | 1.875 | 2.625 | 1.25 | na | na | 3.3542 | 1.0224 | 156.2572 | 105
WT6x95 | 7.25 | 1.0625 | 12.625 | 1.75 | 2.4375 | 1.1875 | na | na | 3.3125 | 1.0097 | 141.3756 | 95
WT6x85 | 7 | 0.9375 | 12.625 | 1.5625 | 2.25 | 1.125 | na | na | 3.2708 | 0.99695 | 126.4939 | 85
WT6x76 | 6.875 | 0.875 | 12.5 | 1.375 | 2.125 | 1.0625 | na | na | 3.2292 | 0.98425 | 113.1005 | 76
WT6x68 | 6.75 | 0.8125 | 12.375 | 1.25 | 1.9375 | 1 | na | na | 3.1875 | 0.97155 | 101.1952 | 68
WT6x60 | 6.5 | 0.6875 | 12.375 | 1.125 | 1.8125 | 1 | 5.5 | 3 | 3.1458 | 0.95885 | 89.2898 | 60
WT6x53 | 6.5 | 0.625 | 12.25 | 1 | 1.6875 | 0.9375 | 5.5 | 3 | 3.125 | 0.9525 | 78.8727 | 53
WT6x48 | 6.375 | 0.5625 | 12.125 | 0.875 | 1.625 | 0.875 | 5.5 | 3 | 3.0833 | 0.9398 | 71.4319 | 48
WT6x43.5 | 6.25 | 0.5 | 12.125 | 0.8125 | 1.5 | 0.875 | 5.5 | 2.75 | 3.0625 | 0.93345 | 64.7351 | 43.5
WT6x39.5 | 6.25 | 0.5 | 12.125 | 0.75 | 1.4375 | 0.875 | 5.5 | 2.75 | 3.0625 | 0.93345 | 58.7825 | 39.5
WT6x36 | 6.125 | 0.4375 | 12 | 0.6875 | 1.375 | 0.875 | 5.5 | 2.75 | 3.0208 | 0.92075 | 53.5739 | 36
WT6x32.5 | 6 | 0.375 | 12 | 0.625 | 1.3125 | 0.8125 | 5.5 | 2.5 | 3 | 0.9144 | 48.3653 | 32.5
0
WT6x29 | 6.125 | 0.375 | 10 | 0.625 | 1.375 | 0.8125 | 5.5 | 2.75 | 2.6875 | 0.81915 | 43.1568 | 29
WT6x26.5 | 6 | 0.375 | 10 | 0.5625 | 1.25 | 0.8125 | 5.5 | 2.5 | 2.6667 | 0.8128 | 39.4363 | 26.5
WT6x25 | 6.125 | 0.375 | 8.125 | 0.625 | 1.375 | 0.8125 | 5.5 | 2.75 | 2.375 | 0.7239 | 37.2041 | 25
WT6x22.5 | 6 | 0.3125 | 8 | 0.5625 | 1.25 | 0.8125 | 5.5 | 2.5 | 2.3333 | 0.7112 | 33.4837 | 22.5
WT6x20 | 6 | 0.3125 | 8 | 0.5 | 1.25 | 0.75 | 5.5 | 2.5 | 2.3333 | 0.7112 | 29.7633 | 20
WT6x17.5 | 6.25 | 0.3125 | 6.5 | 0.5 | 1 | 0.5625 | 3.5 | 2.5 | 2.125 | 0.6477 | 26.0429 | 17.5
WT6x15 | 6.125 | 0.25 | 6.5 | 0.4375 | 0.9375 | 0.5 | 3.5 | 2.5 | 2.1042 | 0.64135 | 22.3225 | 15
WT6x13 | 6.125 | 0.25 | 6.5 | 0.375 | 0.875 | 0.5 | 3.5 | 2.5 | 2.1042 | 0.64135 | 19.3461 | 13
WT6x11 | 6.125 | 0.25 | 4 | 0.4375 | 0.875 | 0.5 | 2.25 | 2.5 | 1.6875 | 0.51435 | 16.3698 | 11
WT6x9.5 | 6.125 | 0.25 | 4 | 0.375 | 0.8125 | 0.5 | 2.25 | 2.25 | 1.6875 | 0.51435 | 14.1376 | 9.5
WT6x8 | 6 | 0.25 | 4 | 0.25 | 0.75 | 0.5 | 2.25 | 2.25 | 1.6667 | 0.508 | 11.9053 | 8
WT6x7 | 6 | 0.1875 | 4 | 0.25 | 0.6875 | 0.5 | 2.25 | 2.25 | 1.6667 | 0.508 | 10.4171 | 7
WT5x56 | 5.625 | 0.75 | 10.375 | 1.25 | 1.875 | 0.9375 | na | na | 2.6667 | 0.8128 | 83.3372 | 56
WT5x50 | 5.5 | 0.6875 | 10.375 | 1.125 | 1.75 | 0.875 | na | na | 2.6458 | 0.80645 | 74.4082 | 50
WT5x44 | 5.375 | 0.625 | 10.25 | 1 | 1.625 | 0.8125 | 5.5 | 2.75 | 2.6042 | 0.79375 | 65.4792 | 44
WT5x38.5 | 5.25 | 0.5 | 10.25 | 0.875 | 1.5 | 0.8125 | 5.5 | 2.75 | 2.5833 | 0.7874 | 57.2943 | 38.5
WT5x34 | 5.25 | 0.5 | 10.125 | 0.75 | 1.375 | 0.75 | 5.5 | 2.75 | 2.5625 | 0.78105 | 50.5976 | 34
WT5x30 | 5.125 | 0.4375 | 10.125 | 0.6875 | 1.3125 | 0.75 | 5.5 | 2.5 | 2.5417 | 0.7747 | 44.6449 | 30
WT5x27 | 5 | 0.375 | 10 | 0.625 | 1.25 | 0.6875 | 5.5 | 2.5 | 2.5 | 0.762 | 40.1804 | 27
WT5x24.5 | 5 | 0.3125 | 10 | 0.5625 | 1.1875 | 0.6875 | 5.5 | 2.5 | 2.5 | 0.762 | 36.46 | 24.5
WT5x22.5 | 5 | 0.375 | 8 | 0.625 | 1.25 | 0.6875 | 5.5 | 2.5 | 2.1667 | 0.6604 | 33.4837 | 22.5
WT5x19.5 | 5 | 0.3125 | 8 | 0.5 | 1.125 | 0.6875 | 5.5 | 2.5 | 2.1667 | 0.6604 | 29.0192 | 19.5
WT5x16.5 | 4.875 | 0.3125 | 8 | 0.4375 | 1.0625 | 0.6875 | 5.5 | 2.25 | 2.1458 | 0.65405 | 24.5547 | 16.5
WT5x15 | 5.25 | 0.3125 | 5.75 | 0.5 | 0.9375 | 0.5 | 2.75 | 2.5 | 1.8333 | 0.5588 | 22.3225 | 15
WT5x13 | 5.125 | 0.25 | 5.75 | 0.4375 | 0.875 | 0.5 | 2.75 | 2.25 | 1.8125 | 0.55245 | 19.3461 | 13
WT5x11 | 5.125 | 0.25 | 5.75 | 0.375 | 0.75 | 0.5 | 2.75 | 2.25 | 1.8125 | 0.55245 | 16.3698 | 11
WT5x9.5 | 5.125 | 0.25 | 4 | 0.375 | 0.8125 | 0.5 | 2.25 | 2.25 | 1.5208 | 0.46355 | 14.1376 | 9.5
WT5x8.5 | 5 | 0.25 | 4 | 0.3125 | 0.75 | 0.5 | 2.25 | 2.25 | 1.5 | 0.4572 | 12.6494 | 8.5
WT5x7.5 | 5 | 0.25 | 4 | 0.25 | 0.6875 | 0.4375 | 2.25 | 2.25 | 1.5 | 0.4572 | 11.1612 | 7.5
WT5x6 | 4.875 | 0.1875 | 4 | 0.1875 | 0.625 | 0.4375 | 2.25 | 2 | 1.4792 | 0.45085 | 8.929 | 6
WT4x33.5 | 4.5 | 0.5625 | 8.25 | 0.9375 | 1.4375 | 0.6875 | na | na | 2.125 | 0.6477 | 49.8535 | 33.5
WT4x29 | 4.375 | 0.5 | 8.25 | 0.8125 | 1.3125 | 0.6875 | 5.5 | 2.75 | 2.1042 | 0.64135 | 43.1568 | 29
WT4x24 | 4.25 | 0.375 | 8.125 | 0.6875 | 1.1875 | 0.625 | 5.5 | 2.5 | 2.0625 | 0.62865 | 35.7159 | 24
WT4x20 | 4.125 | 0.375 | 8.125 | 0.5625 | 1.0625 | 0.625 | 5.5 | 2.5 | 2.0417 | 0.6223 | 29.7633 | 20
WT4x17.5 | 4 | 0.3125 | 8 | 0.5 | 1 | 0.5625 | 5.5 | 2.25 | 2 | 0.6096 | 26.0429 | 17.5
WT4x15.5 | 4 | 0.3125 | 8 | 0.4375 | 0.9375 | 0.5625 | 5.5 | 2.25 | 2 | 0.6096 | 23.0665 | 15.5
WT4x14 | 4 | 0.3125 | 6.5 | 0.4375 | 0.9375 | 0.5625 | 3.5 | 2.25 | 1.75 | 0.5334 | 20.8343 | 14
WT4x12 | 4 | 0.25 | 6.5 | 0.375 | 0.875 | 0.5625 | 3.5 | 2.25 | 1.75 | 0.5334 | 17.858 | 12
WT4x10.5 | 4.125 | 0.25 | 5.25 | 0.375 | 0.8125 | 0.5 | 2.75 | 2.25 | 1.5625 | 0.47625 | 15.6257 | 10.5
WT4x9 | 4.125 | 0.25 | 5.25 | 0.3125 | 0.75 | 0.4375 | 2.75 | 2.25 | 1.5625 | 0.47625 | 13.3935 | 9
WT4x7.5 | 4 | 0.25 | 4 | 0.3125 | 0.75 | 0.5 | 2.25 | 2.25 | 1.3333 | 0.4064 | 11.1612 | 7.5
WT4x6.5 | 4 | 0.25 | 4 | 0.25 | 0.6875 | 0.4375 | 2.25 | 2.25 | 1.3333 | 0.4064 | 9.6731 | 6.5
WT4x5 | 4 | 0.1875 | 4 | 0.1875 | 0.625 | 0.4375 | 2.25 | 2 | 1.3333 | 0.4064 | 7.4408 | 5
WT3x12.5 | 3.25 | 0.3125 | 6.125 | 0.4375 | 0.8125 | 0.4375 | 3.5 | 2.25 | 1.5625 | 0.47625 | 18.6021 | 12.5
WT3x10 | 3.125 | 0.25 | 6 | 0.375 | 0.75 | 0.4375 | 3.5 | 2.25 | 1.5208 | 0.46355 | 14.8816 | 10
WT3x7.5 | 3 | 0.25 | 6 | 0.25 | 0.625 | 0.375 | 3.5 | 2.25 | 1.5 | 0.4572 | 11.1612 | 7.5
WT3x8 | 3.125 | 0.25 | 4 | 0.375 | 0.75 | 0.4375 | 2.25 | 2.25 | 1.1875 | 0.36195 | 11.9053 | 8
WT3x6 | 3 | 0.25 | 4 | 0.25 | 0.625 | 0.375 | 2.25 | 2.25 | 1.1667 | 0.3556 | 8.929 | 6
WT3x4.5 | 3 | 0.1875 | 4 | 0.1875 | 0.5625 | 0.375 | 2.25 | 2 | 1.1667 | 0.3556 | 6.6967 | 4.5
WT2.5x9.5 | 2.625 | 0.25 | 5 | 0.4375 | 0.8125 | 0.4375 | 2.75 | 2.25 | 1.2708 | 0.38735 | 14.1376 | 9.5
WT2.5x8 | 2.5 | 0.25 | 5 | 0.375 | 0.75 | 0.4375 | 2.75 | 2.25 | 1.25 | 0.381 | 11.9053 | 8
WT2x6.5 | 2.125 | 0.25 | 4 | 0.375 | 0.6875 | 0.4375 | 2.25 | 2 | 1.0208 | 0.31115 | 9.6731 | 6.5

## S Tees
2017-06-13 14:31
Flg. Width "bf"
Flg Gage
|  | Avg. Flg. Thk "tf" | [6 empty] | " k"
Web Gage
Depth
Structutral Tees |  |  |  | "d" |  |  | Stem Thk. "tw"
Cut from S shapes
** Flg. Slope 1:6
STee | Depth | Stem Thk. | Flg. Width | *Flg. Thk. | k | Grip | Max | Flange | Web | Sq. Ft.- Surf | Sq.M.- Surf | Weight
Size | d | tw | bf | tf |  |  | Bolt | Bolt Gage | Bolt Gage | Area - per Ft | Area - per M | Kg per M
ST12x60.5 | 12.25 | 0.8125 | 8 | 1.0625 | 2 | 1.125 | 1 |  |  | 3.375 | 1.0287 | 90.0339 | 60.5
ST12x53 | 12.25 | 0.625 | 7.875 | 1.0625 | 2 | 1.125 | 1 |  |  | 3.3542 | 1.0224 | 78.8727 | 53
ST12x50 | 12 | 0.75 | 7.25 | 0.875 | 1.75 | 0.875 | 1 | 4 | 3 | 3.2083 | 0.9779 | 74.4082 | 50
ST12x45 | 12 | 0.625 | 7.125 | 0.875 | 1.75 | 0.875 | 1 | 4 | 3 | 3.1875 | 0.97155 | 66.9674 | 45
ST12x40 | 12 | 0.5 | 7 | 0.875 | 1.75 | 0.875 | 1 |  |  | 3.1667 | 0.9652 | 59.5266 | 40
ST10x48 | 10.125 | 0.8125 | 7.25 | 0.9375 | 1.75 | 0.9375 | 1 |  |  | 2.8958 | 0.88265 | 71.4319 | 48
ST10x43 | 10.125 | 0.6875 | 7 | 0.9375 | 1.75 | 0.9375 | 1 |  |  | 2.8542 | 0.86995 | 63.9911 | 43
ST10x37.5 | 10 | 0.625 | 6.375 | 0.8125 | 1.625 | 0.8125 | 0.875 | 3.5 | 3 | 2.7292 | 0.83185 | 55.8062 | 37.5
ST10x33 | 10 | 0.5 | 6.25 | 0.8125 | 1.625 | 0.8125 | 0.875 |  |  | 2.7083 | 0.8255 | 49.1094 | 33
ST9x35 | 9 | 0.6875 | 6.25 | 0.6875 | 1.5 | 0.6875 | 0.875 | 3.5 | 2.75 | 2.5417 | 0.7747 | 52.0857 | 35
ST9x27.35 | 9 | 0.4375 | 6 | 0.6875 | 1.5 | 0.6875 | 0.875 | 3.5 | 2.75 | 2.5 | 0.762 | 40.7013 | 27.35
ST7.5x25 | 7.5 | 0.5625 | 5.625 | 0.625 | 1.375 | 0.5625 | 0.75 | 3.5 | 2.75 | 2.1875 | 0.66675 | 37.2041 | 25
ST7.5x21.45 | 7.5 | 0.4375 | 5.5 | 0.625 | 1.375 | 0.5625 | 0.75 | 3.5 | 2.75 | 2.1667 | 0.6604 | 31.9211 | 21.45
ST6x25 | 6 | 0.6875 | 5.5 | 0.6875 | 1.4375 | 0.6875 | 0.75 | 3 | 2.75 | 1.9167 | 0.5842 | 37.2041 | 25
ST6x20.4 | 6 | 0.4375 | 5.25 | 0.6875 | 1.4375 | 0.625 | 0.75 | 3 | 2.75 | 1.875 | 0.5715 | 30.3585 | 20.4
ST6x17.5 | 6 | 0.4375 | 5.125 | 0.5625 | 1.1875 | 0.5 | 0.75 | 3 | 2.5 | 1.8542 | 0.56515 | 26.0429 | 17.5
ST6x15.9 | 6 | 0.375 | 5 | 0.5625 | 1.1875 | 0.5 | 0.75 | 3 | 2.5 | 1.8333 | 0.5588 | 23.6618 | 15.9
ST5x17.5 | 5 | 0.625 | 5 | 0.5 | 1.125 | 0.5 | 0.75 | 2.75 | 2.5 | 1.6667 | 0.508 | 26.0429 | 17.5
ST5x12.7 | 5 | 0.3125 | 4.625 | 0.5 | 1.125 | 0.5 | 0.75 | 2.75 | 2.5 | 1.6042 | 0.48895 | 18.8997 | 12.7
ST4x11.5 | 4 | 0.4375 | 4.125 | 0.4375 | 1 | 0.4375 | 0.75 | 2.25 | 2.5 | 1.3542 | 0.41275 | 17.1139 | 11.5
ST4x9.2 | 4 | 0.25 | 4 | 0.4375 | 1 | 0.4375 | 0.75 | 2.25 | 2.5 | 1.3333 | 0.4064 | 13.6911 | 9.2
ST3.5x10 | 3.5 | 0.4375 | 3.875 | 0.375 | 0.9375 | 0.375 | 0.625 |  |  | 1.2292 | 0.37465 | 14.8816 | 10
ST3.5x7.65 | 3.5 | 0.25 | 3.625 | 0.375 | 0.9375 | 0.375 | 0.625 | 2.25 | 2.5 | 1.1875 | 0.36195 | 96.7307 | 65
ST3x8.625 | 3 | 0.4375 | 3.625 | 0.375 | 0.875 | 0.375 | 0.625 | 2 | 2.25 | 1.1042 | 0.33655 | 12.8354 | 8.625
ST3x6.25 | 3 | 0.25 | 3.375 | 0.375 | 0.875 | 0.375 | - | - | 2.25 | 1.0625 | 0.32385 | 9.301 | 6.25
ST2.5x7.375 | 2.5 | 0.5 | 3.25 | 0.3125 | 0.8125 | 0.3125 | - |  |  | 0.95833 | 0.2921 | 10.9752 | 7.375
ST2.5x5 | 2.5 | 0.1875 | 3 | 0.3125 | 0.8125 | 0.3125 | - | - | 2.25 | 0.91667 | 0.2794 | 7.4408 | 5
ST2x4.75 | 2 | 0.3125 | 2.75 | 0.3125 | 0.75 | 0.3125 | - | - | 2 | 0.79167 | 0.2413 | 7.0688 | 4.75
ST2x3.85 | 2 | 0.1875 | 2.625 | 0.3125 | 0.75 | 0.3125 | - | - | 2 | 0.77083 | 0.23495 | 5.7294 | 3.85
ST1.5x3.75 | 1.5 | 0.375 | 2.5 | 0.25 | 0.6875 | 0.25 | - | - | - | 0.66667 | 0.2032 | 5.5806 | 3.75
ST1.5x2.85 | 1.5 | 0.1875 | 2.375 | 0.25 | 0.6875 | 0.25 | - | - | - | 0.64583 | 0.19685 |  | 2.85

## Tubing
2017-06-13 14:31
Structural Tubing | [5 empty] | Radius Equals two times wall thickness
Square | [6 empty] | Rectangular
Nominal | Wall | Weight | Weight | Surf. Area | Surf. Area |  | Nominal | Wall | Weight | Weight | Surf. Area | Surf. Area
Size | Thk | Lbs/Ft | Kg./M | Sq.Ft-per Ft | Sq.M-per M |  | Size | Thk | Lbs/Ft | Kg./M | Sq.Ft-per Ft | Sq.M-per M
16x16 | 0.625 | 127.37 | 189.5475 | 5.3333 | 1.6256 |  | 20x12 | 0.5 | 103.3 | 153.7273 | 5.3333 | 1.6256
16x16 | 0.5 | 103.3 | 153.7273 | 5.3333 | 1.6256 |  | 20x12 | 0.375 | 78.52 | 116.8506 | 5.3333 | 1.6256
16x16 | 0.375 | 78.52 | 116.8506 | 5.3333 | 1.6256 |  | 20x12 | 0.3125 | 65.87 | 98.0254 | 5.3333 | 1.6256
16x16 | 0.3125 | 65.87 | 98.0254 | 5.3333 | 1.6256
[7 empty] | 20x8 | 0.5 | 89.68 | 133.4586 | 4.6667 | 1.4224
14x14 | 0.625 | 110.36 | 164.2338 | 4.6667 | 1.4224 |  | 20x8 | 0.375 | 68.31 | 101.6565 | 4.6667 | 1.4224
14x14 | 0.5 | 89.68 | 133.4586 | 4.6667 | 1.4224 |  | 20x8 | 0.3125 | 57.36 | 85.3611 | 4.6667 | 1.4224
14x14 | 0.375 | 68.31 | 101.6565 | 4.6667 | 1.4224
14x14 | 0.3125 | 57.36 | 85.3611 | 4.6667 | 1.4224 |  | 20x4 | 0.5 | 76.07 | 113.2046 | 4 | 1.2192
[7 empty] | 20x4 | 0.375 | 58.1 | 86.4623 | 4 | 1.2192
12x12 | 0.625 | 93.34 | 138.9052 | 4 | 1.2192 |  | 20x4 | 0.3125 | 48.86 | 72.7117 | 4 | 1.2192
12x12 | 0.5 | 76.07 | 113.2046 | 4 | 1.2192
12x12 | 0.375 | 58.1 | 86.4623 | 4 | 1.2192 |  | 18x6 | 0.5 | 76.07 | 113.2046 | 4 | 1.2192
12x12 | 0.3125 | 48.86 | 72.7117 | 4 | 1.2192 |  | 18x6 | 0.375 | 58.1 | 86.4623 | 4 | 1.2192
12x12 | 0.25 | 39.43 | 58.6783 | 4 | 1.2192 |  | 18x6 | 0.3125 | 48.86 | 72.7117 | 4 | 1.2192
12x12 | 0.1875 | 29.84 | 44.4068 | 4 | 1.2192
[7 empty] | 16x12 | 0.625 | 110.36 | 164.2338 | 4.6667 | 1.4224
10x10 | 0.625 | 76.33 | 113.5916 | 3.3333 | 1.016 |  | 16x12 | 0.5 | 89.68 | 133.4586 | 4.6667 | 1.4224
10x10 | 0.5625 | 69.48 | 103.3976 | 3.3333 | 1.016 |  | 16x12 | 0.375 | 68.31 | 101.6565 | 4.6667 | 1.4224
10x10 | 0.5 | 62.46 | 92.9507 | 3.3333 | 1.016 |  | 16x12 | 0.3125 | 57.36 | 85.3611 | 4.6667 | 1.4224
10x10 | 0.375 | 47.9 | 71.2831 | 3.3333 | 1.016
10x10 | 0.3125 | 40.35 | 60.0474 | 3.3333 | 1.016 |  | 16x8 | 0.5 | 76.07 | 113.2046 | 4 | 1.2192
10x10 | 0.25 | 32.63 | 48.5588 | 3.3333 | 1.016 |  | 16x8 | 0.375 | 58.1 | 86.4623 | 4 | 1.2192
10x10 | 0.1875 | 24.73 | 36.8023 | 3.3333 | 1.016 |  | 16x8 | 0.3125 | 48.86 | 72.7117 | 4 | 1.2192
9x9 | 0.625 | 67.82 | 100.9273 | 3 | 0.9144 |  | 16x4 | 0.5 | 62.46 | 92.9507 | 3.3333 | 1.016
9x9 | 0.5625 | 61.83 | 92.0132 | 3 | 0.9144 |  | 16x4 | 0.375 | 47.9 | 71.2831 | 3.3333 | 1.016
9x9 | 0.5 | 55.66 | 82.8312 | 3 | 0.9144 |  | 16x4 | 0.3125 | 40.35 | 60.0474 | 3.3333 | 1.016
9x9 | 0.375 | 42.79 | 63.6785 | 3 | 0.9144
9x9 | 0.3125 | 36.1 | 53.7227 | 3 | 0.9144 |  | 14x10 | 0.625 | 93.34 | 138.9052 | 4 | 1.2192
9x9 | 0.25 | 29.23 | 43.499 | 3 | 0.9144 |  | 14x10 | 0.5 | 76.07 | 113.2046 | 4 | 1.2192
9x9 | 0.1875 | 22.18 | 33.0075 | 3 | 0.9144 |  | 14x10 | 0.375 | 58.1 | 86.4623 | 4 | 1.2192
[7 empty] | 14x10 | 0.3125 | 48.86 | 72.7117 | 4 | 1.2192
8x8 | 0.625 | 59.32 | 88.2779 | 2.6667 | 0.8128
8x8 | 0.5625 | 54.17 | 80.6138 | 2.6667 | 0.8128 |  | 14x6 | 0.5 | 62.46 | 92.9507 | 3.3333 | 1.016
8x8 | 0.5 | 48.85 | 72.6968 | 2.6667 | 0.8128 |  | 14x6 | 0.375 | 47.9 | 71.2831 | 3.3333 | 1.016
8x8 | 0.375 | 37.69 | 56.0889 | 2.6667 | 0.8128 |  | 14x6 | 0.3125 | 40.35 | 60.0474 | 3.3333 | 1.016
8x8 | 0.3125 | 31.84 | 47.3831 | 2.6667 | 0.8128 |  | 14x6 | 0.25 | 32.63 | 48.5588 | 3.3333 | 1.016
8x8 | 0.25 | 25.82 | 38.4244 | 2.6667 | 0.8128
8x8 | 0.1875 | 19.63 | 29.2127 | 2.6667 | 0.8128 |  | 14x4 | 0.5 | 55.66 | 82.8312 | 3 | 0.9144
[7 empty] | 14x4 | 0.375 | 42.79 | 63.6785 | 3 | 0.9144
7x7 | 0.5625 | 46.51 | 69.2145 | 2.3333 | 0.7112 |  | 14x4 | 0.3125 | 36.1 | 53.7227 | 3 | 0.9144
7x7 | 0.5 | 42.05 | 62.5773 | 2.3333 | 0.7112 |  | 14x4 | 0.25 | 29.23 | 43.499 | 3 | 0.9144
7x7 | 0.375 | 32.58 | 48.4844 | 2.3333 | 0.7112
7x7 | 0.3125 | 27.59 | 41.0584 | 2.3333 | 0.7112 |  | 12x8 | 0.625 | 76.33 | 113.5916 | 3.3333 | 1.016
7x7 | 0.25 | 22.42 | 33.3646 | 2.3333 | 0.7112 |  | 12x8 | 0.5625 | 69.48 | 103.3976 | 3.3333 | 1.016
7x7 | 0.1875 | 17.08 | 25.4178 | 2.3333 | 0.7112 |  | 12x8 | 0.5 | 62.46 | 92.9507 | 3.3333 | 1.016
[7 empty] | 12x8 | 0.375 | 47.9 | 71.2831 | 3.3333 | 1.016
6x6 | 0.5625 | 38.86 | 57.8301 | 2 | 0.6096 |  | 12x8 | 0.3125 | 40.35 | 60.0474 | 3.3333 | 1.016
6x6 | 0.5 | 35.24 | 52.4429 | 2 | 0.6096 |  | 12x8 | 0.25 | 32.63 | 48.5588 | 3.3333 | 1.016
6x6 | 0.375 | 27.48 | 40.8947 | 2 | 0.6096 |  | 12x8 | 0.1875 | 24.73 | 36.8023 | 3.3333 | 1.016
6x6 | 0.3125 | 23.34 | 34.7337 | 2 | 0.6096
6x6 | 0.25 | 19.02 | 28.3049 | 2 | 0.6096 |  | 12x6 | 0.625 | 67.82 | 100.9273 | 3 | 0.9144
6x6 | 0.1875 | 14.53 | 21.623 | 2 | 0.6096 |  | 12x6 | 0.5625 | 61.83 | 92.0132 | 3 | 0.9144
[7 empty] | 12x6 | 0.5 | 55.66 | 82.8312 | 3 | 0.9144
5x5 | 0.5 | 28.43 | 42.3085 | 1.6667 | 0.508 |  | 12x6 | 0.375 | 42.79 | 63.6785 | 3 | 0.9144
5x5 | 0.375 | 22.37 | 33.2902 | 1.6667 | 0.508 |  | 12x6 | 0.3125 | 36.1 | 53.7227 | 3 | 0.9144
5x5 | 0.3125 | 19.08 | 28.3942 | 1.6667 | 0.508 |  | 12x6 | 0.25 | 29.23 | 43.499 | 3 | 0.9144
5x5 | 0.25 | 15.62 | 23.2451 | 1.6667 | 0.508 |  | 12x6 | 0.1875 | 22.18 | 33.0075 | 3 | 0.9144
5x5 | 0.1875 | 11.97 | 17.8133 | 1.6667 | 0.508
[7 empty] | 12x4 | 0.625 | 59.32 | 88.2779 | 2.6667 | 0.8128
4.5x4.5 | 0.25 | 13.91 | 20.7004 | 1.5 | 0.4572 |  | 12x4 | 0.5625 | 54.17 | 80.6138 | 2.6667 | 0.8128
4.5x4.5 | 0.1875 | 10.7 | 15.9234 | 1.5 | 0.4572 |  | 12x4 | 0.5 | 48.85 | 72.6968 | 2.6667 | 0.8128
[7 empty] | 12x4 | 0.375 | 37.69 | 56.0889 | 2.6667 | 0.8128
4x4 | 0.5 | 21.63 | 32.189 | 1.3333 | 0.4064 |  | 12x4 | 0.3125 | 31.84 | 47.3831 | 2.6667 | 0.8128
4x4 | 0.375 | 17.27 | 25.7006 | 1.3333 | 0.4064 |  | 12x4 | 0.25 | 25.82 | 38.4244 | 2.6667 | 0.8128
4x4 | 0.3125 | 14.83 | 22.0695 | 1.3333 | 0.4064 |  | 12x4 | 0.1875 | 19.63 | 29.2127 | 2.6667 | 0.8128
4x4 | 0.25 | 12.21 | 18.1705 | 1.3333 | 0.4064
4x4 | 0.1875 | 9.42 | 14.0185 | 1.3333 | 0.4064 |  | 12x2 | 0.25 | 22.42 | 33.3646 | 2.3333 | 0.7112
[7 empty] | 12x2 | 0.1875 | 17.08 | 25.4178 | 2.3333 | 0.7112
3.5x3.5 | 0.3125 | 12.7 | 18.8997 | 1.1667 | 0.3556
3.5x3.5 | 0.25 | 10.51 | 15.6406 | 1.1667 | 0.3556 |  | 10x8 | 0.625 | 67.82 | 100.9273 | 3 | 0.9144
3.5x3.5 | 0.1875 | 8.15 | 12.1285 | 1.1667 | 0.3556 |  | 10x8 | 0.5625 | 61.83 | 92.0132 | 3 | 0.9144
[7 empty] | 10x8 | 0.5 | 55.66 | 82.8312 | 3 | 0.9144
3x3 | 0.3125 | 10.58 | 15.7448 | 1 | 0.3048 |  | 10x8 | 0.375 | 42.79 | 63.6785 | 3 | 0.9144
3x3 | 0.25 | 8.81 | 13.1107 | 1 | 0.3048 |  | 10x8 | 0.3125 | 36.1 | 53.7227 | 3 | 0.9144
3x3 | 0.1875 | 6.87 | 10.2237 | 1 | 0.3048 |  | 10x8 | 0.25 | 29.23 | 43.499 | 3 | 0.9144
[7 empty] | 10x8 | 0.1875 | 22.18 | 33.0075 | 3 | 0.9144
2.5x2.5 | 0.3125 | 8.45 | 12.575 | 0.83333 | 0.254
2.5x2.5 | 0.25 | 7.11 | 10.5808 | 0.83333 | 0.254 |  | 10x6 | 0.625 | 59.32 | 88.2779 | 2.6667 | 0.8128
2.5x2.5 | 0.1875 | 5.59 | 8.3188 | 0.83333 | 0.254 |  | 10x6 | 0.5625 | 54.17 | 80.6138 | 2.6667 | 0.8128
[7 empty] | 10x6 | 0.5 | 48.85 | 72.6968 | 2.6667 | 0.8128
2x2 | 0.3125 | 6.32 | 9.4052 | 0.66667 | 0.2032 |  | 10x6 | 0.375 | 37.69 | 56.0889 | 2.6667 | 0.8128
2x2 | 0.25 | 5.41 | 8.051 | 0.66667 | 0.2032 |  | 10x6 | 0.3125 | 31.84 | 47.3831 | 2.6667 | 0.8128
2x2 | 0.1875 | 4.32 | 6.4289 | 0.66667 | 0.2032 |  | 10x6 | 0.25 | 25.82 | 38.4244 | 2.6667 | 0.8128
[7 empty] | 10x6 | 0.1875 | 19.63 | 29.2127 | 2.6667 | 0.8128
[7 empty] | 10x5 | 0.625 | 55.06 | 81.9383 | 2.5 | 0.762
[7 empty] | 10x5 | 0.5625 | 50.34 | 74.9142 | 2.5 | 0.762
[7 empty] | 10x5 | 0.5 | 45.45 | 67.6371 | 2.5 | 0.762
[7 empty] | 10x5 | 0.375 | 35.13 | 52.2792 | 2.5 | 0.762
[7 empty] | 10x5 | 0.3125 | 29.72 | 44.2282 | 2.5 | 0.762
[7 empty] | 10x5 | 0.25 | 24.12 | 35.8945 | 2.5 | 0.762
[7 empty] | 10x5 | 0.1875 | 18.35 | 27.3078 | 2.5 | 0.762
[7 empty] | 10x4 | 0.5625 | 46.51 | 69.2145 | 2.3333 | 0.7112
[7 empty] | 10x4 | 0.5 | 42.05 | 62.5773 | 2.3333 | 0.7112
[7 empty] | 10x4 | 0.375 | 32.58 | 48.4844 | 2.3333 | 0.7112
[7 empty] | 10x4 | 0.3125 | 27.59 | 41.0584 | 2.3333 | 0.7112
[7 empty] | 10x4 | 0.25 | 22.42 | 33.3646 | 2.3333 | 0.7112
[7 empty] | 10x4 | 0.1875 | 17.08 | 25.4178 | 2.3333 | 0.7112
[7 empty] | 10x2 | 0.375 | 27.48 | 40.8947 | 2 | 0.6096
[7 empty] | 10x2 | 0.3125 | 23.34 | 34.7337 | 2 | 0.6096
[7 empty] | 10x2 | 0.25 | 19.02 | 28.3049 | 2 | 0.6096
[7 empty] | 10x2 | 0.1875 | 14.53 | 21.623 | 2 | 0.6096
[7 empty] | 9x7 | 0.625 | 59.32 | 88.2779 | 2.6667 | 0.8128
[7 empty] | 9x7 | 0.5625 | 54.17 | 80.6138 | 2.6667 | 0.8128
[7 empty] | 9x7 | 0.5 | 48.85 | 72.6968 | 2.6667 | 0.8128
[7 empty] | 9x7 | 0.375 | 37.69 | 56.0889 | 2.6667 | 0.8128
[7 empty] | 9x7 | 0.3125 | 31.84 | 47.3831 | 2.6667 | 0.8128
[7 empty] | 9x7 | 0.25 | 25.82 | 38.4244 | 2.6667 | 0.8128
[7 empty] | 9x7 | 0.1875 | 19.63 | 29.2127 | 2.6667 | 0.8128
[7 empty] | 9x6 | 0.625 | 55.06 | 81.9383 | 2.5 | 0.762
[7 empty] | 9x6 | 0.5625 | 50.34 | 74.9142 | 2.5 | 0.762
[7 empty] | 9x6 | 0.5 | 45.45 | 67.6371 | 2.5 | 0.762
[7 empty] | 9x6 | 0.375 | 35.13 | 52.2792 | 2.5 | 0.762
[7 empty] | 9x6 | 0.3125 | 29.72 | 44.2282 | 2.5 | 0.762
[7 empty] | 9x6 | 0.25 | 24.12 | 35.8945 | 2.5 | 0.762
[7 empty] | 9x6 | 0.1875 | 18.35 | 27.3078 | 2.5 | 0.762
[7 empty] | 9x5 | 0.5625 | 46.51 | 69.2145 | 2.3333 | 0.7112
[7 empty] | 9x5 | 0.5 | 42.05 | 62.5773 | 2.3333 | 0.7112
[7 empty] | 9x5 | 0.375 | 32.58 | 48.4844 | 2.3333 | 0.7112
[7 empty] | 9x5 | 0.3125 | 27.59 | 41.0584 | 2.3333 | 0.7112
[7 empty] | 9x5 | 0.25 | 22.42 | 33.3646 | 2.3333 | 0.7112
[7 empty] | 9x5 | 0.1875 | 17.08 | 25.4178 | 2.3333 | 0.7112
[7 empty] | 9x3 | 0.5 | 35.24 | 52.4429 | 2 | 0.6096
[7 empty] | 9x3 | 0.375 | 27.48 | 40.8947 | 2 | 0.6096
[7 empty] | 9x3 | 0.3125 | 23.34 | 34.7337 | 2 | 0.6096
[7 empty] | 9x3 | 0.25 | 19.02 | 28.3049 | 2 | 0.6096
[7 empty] | 9x3 | 0.1875 | 14.53 | 21.623 | 2 | 0.6096
[7 empty] | 8x6 | 0.5625 | 46.51 | 69.2145 | 2.3333 | 0.7112
[7 empty] | 8x6 | 0.5 | 42.05 | 62.5773 | 2.3333 | 0.7112
[7 empty] | 8x6 | 0.375 | 32.58 | 48.4844 | 2.3333 | 0.7112
[7 empty] | 8x6 | 0.3125 | 27.59 | 41.0584 | 2.3333 | 0.7112
[7 empty] | 8x6 | 0.25 | 22.42 | 33.3646 | 2.3333 | 0.7112
[7 empty] | 8x6 | 0.1875 | 17.08 | 25.4178 | 2.3333 | 0.7112
[7 empty] | 8x4 | 0.5625 | 38.86 | 57.8301 | 2 | 0.6096
[7 empty] | 8x4 | 0.5 | 35.24 | 52.4429 | 2 | 0.6096
[7 empty] | 8x4 | 0.375 | 27.48 | 40.8947 | 2 | 0.6096
[7 empty] | 8x4 | 0.3125 | 23.34 | 34.7337 | 2 | 0.6096
[7 empty] | 8x4 | 0.25 | 19.02 | 28.3049 | 2 | 0.6096
[7 empty] | 8x4 | 0.1875 | 14.53 | 21.623 | 2 | 0.6096
[7 empty] | 8x3 | 0.5 | 31.84 | 47.3831 | 1.8333 | 0.5588
[7 empty] | 8x3 | 0.375 | 24.93 | 37.0999 | 1.8333 | 0.5588
[7 empty] | 8x3 | 0.3125 | 21.21 | 31.564 | 1.8333 | 0.5588
[7 empty] | 8x3 | 0.25 | 17.32 | 25.775 | 1.8333 | 0.5588
[7 empty] | 8x3 | 0.1875 | 13.25 | 19.7182 | 1.8333 | 0.5588
[7 empty] | 8x2 | 0.375 | 22.37 | 33.2902 | 1.6667 | 0.508
[7 empty] | 8x2 | 0.3125 | 19.08 | 28.3942 | 1.6667 | 0.508
[7 empty] | 8x2 | 0.25 | 15.62 | 23.2451 | 1.6667 | 0.508
[7 empty] | 8x2 | 0.1875 | 11.97 | 17.8133 | 1.6667 | 0.508
[7 empty] | 7x5 | 0.5 | 35.24 | 52.4429 | 2 | 0.6096
[7 empty] | 7x5 | 0.375 | 27.48 | 40.8947 | 2 | 0.6096
[7 empty] | 7x5 | 0.3125 | 23.34 | 34.7337 | 2 | 0.6096
[7 empty] | 7x5 | 0.25 | 19.02 | 28.3049 | 2 | 0.6096
[7 empty] | 7x5 | 0.1875 | 14.53 | 21.623 | 2 | 0.6096
[7 empty] | 7x4 | 0.5 | 31.84 | 47.3831 | 1.8333 | 0.5588
[7 empty] | 7x4 | 0.375 | 24.93 | 37.0999 | 1.8333 | 0.5588
[7 empty] | 7x4 | 0.3125 | 21.21 | 31.564 | 1.8333 | 0.5588
[7 empty] | 7x4 | 0.25 | 17.32 | 25.775 | 1.8333 | 0.5588
[7 empty] | 7x4 | 0.1875 | 13.25 | 19.7182 | 1.8333 | 0.5588
[7 empty] | 7x3 | 0.5 | 28.43 | 42.3085 | 1.6667 | 0.508
[7 empty] | 7x3 | 0.375 | 22.37 | 33.2902 | 1.6667 | 0.508
[7 empty] | 7x3 | 0.3125 | 19.08 | 28.3942 | 1.6667 | 0.508
[7 empty] | 7x3 | 0.25 | 15.62 | 23.2451 | 1.6667 | 0.508
[7 empty] | 7x3 | 0.1875 | 11.97 | 17.8133 | 1.6667 | 0.508
[7 empty] | 7x2 | 0.25 | 13.91 | 20.7004 | 1.5 | 0.4572
[7 empty] | 7x2 | 0.1875 | 10.7 | 15.9234 | 1.5 | 0.4572
[7 empty] | 6x5 | 0.5 | 31.84 | 47.3831 | 1.8333 | 0.5588
[7 empty] | 6x5 | 0.375 | 24.93 | 37.0999 | 1.8333 | 0.5588
[7 empty] | 6x5 | 0.3125 | 21.21 | 31.564 | 1.8333 | 0.5588
[7 empty] | 6x5 | 0.25 | 17.32 | 25.775 | 1.8333 | 0.5588
[7 empty] | 6x5 | 0.1875 | 13.25 | 19.7182 | 1.8333 | 0.5588
[7 empty] | 6x4 | 0.5 | 28.43 | 42.3085 | 1.6667 | 0.508
[7 empty] | 6x4 | 0.375 | 22.37 | 33.2902 | 1.6667 | 0.508
[7 empty] | 6x4 | 0.3125 | 19.08 | 28.3942 | 1.6667 | 0.508
[7 empty] | 6x4 | 0.25 | 15.62 | 23.2451 | 1.6667 | 0.508
[7 empty] | 6x4 | 0.1875 | 11.97 | 17.8133 | 1.6667 | 0.508
[7 empty] | 6x3 | 0.375 | 19.82 | 29.4954 | 1.5 | 0.4572
[7 empty] | 6x3 | 0.3125 | 16.96 | 25.2393 | 1.5 | 0.4572
[7 empty] | 6x3 | 0.25 | 13.91 | 20.7004 | 1.5 | 0.4572
[7 empty] | 6x3 | 0.1875 | 10.7 | 15.9234 | 1.5 | 0.4572
[7 empty] | 6x2 | 0.375 | 17.27 | 25.7006 | 1.3333 | 0.4064
[7 empty] | 6x2 | 0.3125 | 14.83 | 22.0695 | 1.3333 | 0.4064
[7 empty] | 6x2 | 0.25 | 12.21 | 18.1705 | 1.3333 | 0.4064
[7 empty] | 6x2 | 0.1875 | 9.42 | 14.0185 | 1.3333 | 0.4064
[7 empty] | 5x4 | 0.375 | 19.82 | 29.4954 | 1.5 | 0.4572
[7 empty] | 5x4 | 0.3125 | 16.96 | 25.2393 | 1.5 | 0.4572
[7 empty] | 5x4 | 0.25 | 13.91 | 20.7004 | 1.5 | 0.4572
[7 empty] | 5x4 | 0.1875 | 10.7 | 15.9234 | 1.5 | 0.4572
[7 empty] | 5x3 | 0.5 | 21.63 | 32.189 | 1.3333 | 0.4064
[7 empty] | 5x3 | 0.375 | 17.27 | 25.7006 | 1.3333 | 0.4064
[7 empty] | 5x3 | 0.3125 | 14.83 | 22.0695 | 1.3333 | 0.4064
[7 empty] | 5x3 | 0.25 | 12.21 | 18.1705 | 1.3333 | 0.4064
[7 empty] | 5x3 | 0.1875 | 9.42 | 14.0185 | 1.3333 | 0.4064
[7 empty] | 5x2 | 0.3125 | 12.7 | 18.8997 | 1.1667 | 0.3556
[7 empty] | 5x2 | 0.25 | 10.51 | 15.6406 | 1.1667 | 0.3556
[7 empty] | 5x2 | 0.1875 | 8.15 | 12.1285 | 1.1667 | 0.3556
[7 empty] | 4x3 | 0.3125 | 12.7 | 18.8997 | 1.1667 | 0.3556
[7 empty] | 4x3 | 0.25 | 10.51 | 15.6406 | 1.1667 | 0.3556
[7 empty] | 4x3 | 0.1875 | 8.15 | 12.1285 | 1.1667 | 0.3556
[7 empty] | 4x2 | 0.3125 | 10.58 | 15.7448 | 1 | 0.3048
[7 empty] | 4x2 | 0.25 | 8.81 | 13.1107 | 1 | 0.3048
[7 empty] | 4x2 | 0.1875 | 6.87 | 10.2237 | 1 | 0.3048
[7 empty] | 3.5x2.5 | 0.25 | 8.81 | 13.1107 | 1 | 0.3048
[7 empty] | 3.5x2.5 | 0.1875 | 6.87 | 10.2237 | 1 | 0.3048
[7 empty] | 3x2 | 0.25 | 7.11 | 10.5808 | 0.83333 | 0.254
[7 empty] | 3x2 | 0.1875 | 5.59 | 8.3188 | 0.83333 | 0.254

## Grating
2017-06-13 14:31
Welded Steel Grating
Bearing Bars Spaced 1 3/16" on centers - Cross bars 4" on center
Note: | Spans and loads in the shaded area exceeds a deflection of 1/4" for uniform loads
of 100#/sq. ft. which provide safe pedestrian comfort, but can be exceeded for other
types of loads at the discretion of the engineer.
U- | Safe Uniform Load in lbs per sq. ft.
C- | Safe Concentrated Loads in lbs per foot of Grating Width
D- | Deflection in inches
Bearing Bar | Nominal Wt. | U | [5 empty] | Span
lbs per sq.ft.
Size | Kg per sq. M | D | 2'-0" | 2'-6" | 3'-0" | 3'-6" | 4'-0" | 4'-6" | 5'-0" | 5'-6" | 6'-0 | 6'-6" | 7'-0" | 8'-0" | 9'-0"
|  | U | 386 | 247 | 172 | 126 | 96 | 76 | [6 empty] | .
3/4" x 1/8" | 4 | D | 0.095 | 0.151 | 0.216 | 0.295 | 0.374 | 0.486
| 19.5297 | C | 386 | 308 | 258 | 220 | 194 | 171
|  | D | 0.076 | 0.119 | 0.173 | 0.234 | 0.308 | 0.389
|  | U | 578 | 370 | 258 | 188 | 144 | 115
3/4"x3/16" | 5.6 | D | 0.095 | 0.151 | 0.216 | 0.295 | 0.374 | 0.486
| 27.3416 | C | 578 | 462 | 386 | 331 | 289 | 257
|  | D | 0.076 | 0.119 | 0.173 | 0.234 | 0.38 | 0.389
|  | U | 686 | 439 | 304 | 224 | 171 | 135 | 109 | 91 | 76
1"x1/8" | 5.1 | D | 0.072 | 0.111 | 0.159 | 0.219 | 0.288 | 0.366 | 0.451 | 0.547 | 0.673
| 24.9004 | C | 686 | 549 | 457 | 392 | 343 | 305 | 275 | 250 | 228
|  | D | 0.057 | 0.09 | 0.129 | 0.176 | 0.231 | 0.293 | 0.36 | 0.434 | 0.518
|  | U | 1029 | 659 | 459 | 338 | 257 | 203 | 164 | 135 | 114
1"x3/16" | 7.3 | D | 0.072 | 0.111 | 0.159 | 0.219 | 0.288 | 0.366 | 0.451 | 0.547 | 0.673
| 35.6417 | C | 1029 | 824 | 686 | 587 | 514 | 458 | 412 | 375 | 343
|  | D | 0.057 | 0.09 | 0.129 | 0.176 | 0.231 | 0.293 | 0.36 | 0.434 | 0.518
|  | U | 1072 | 686 | 476 | 350 | 268 | 212 | 172 | 142 | 119 | 101 | 87
1-1/4"x1/8" | 6.1 | D | 0.057 | 0.09 | 0.129 | 0.176 | 0.231 | 0.291 | 0.358 | 0.433 | 0.52 | 0.608 | 0.704
| 29.7828 | C | 1072 | 858 | 716 | 613 | 536 | 477 | 430 | 390 | 358 | 330 | 306
|  | D | 0.046 | 0.072 | 0.104 | 0.141 | 0.183 | 0.233 | 0.288 | 0.349 | 0.416 | 0.487 | 0.565
|  | U | 1608 | 1028 | 716 | 526 | 403 | 318 | 258 | 213 | 179 | 152 | 131
1-1/4"x3/16" | 8.9 | D | 0.057 | 0.09 | 0.129 | 0.176 | 0.231 | 0.291 | 0.358 | 0.433 | 0.52 | 0.608 | 0.704
| 43.4536 | C | 1608 | 1285 | 1073 | 918 | 803 | 716 | 644 | 585 | 536 | 495 | 459
|  | D | 0.046 | 0.072 | 0.104 | 0.141 | 0.183 | 0.233 | 0.288 | 0.349 | 0.416 | 0.487 | 0.565
|  | U | 1544 | 0.987 | 686 | 505 | 387 | 306 | 248 | 205 | 172 | 149 | 128 | 96 | 75
1-1/2"x1/8" | 7.3 | D | 0.047 | 0.075 | 0.106 | 0.147 | 0.192 | 0.243 | 0.3 | 0.365 | 0.433 | 0.506 | 0.587 | 774 | 0.978
| 35.6417 | C | 1544 | 1235 | 1029 | 883 | 772 | 687 | 619 | 563 | 515 | 475 | 441 | 386 | 342
|  | D | 0.038 | 0.059 | 0.087 | 0.117 | 0.154 | 0.195 | 0.241 | 0.289 | 0.347 | 0.406 | 0.47 | 614 | 0.777
|  | U | 2321 | 1485 | 1031 | 758 | 581 | 458 | 371 | 307 | 260 | 222 | 191 | 145 | 115
1-1/2"x3/16" | 10.6 | D | 0.047 | 0.075 | 0.106 | 0.147 | 0.192 | 0.243 | 0.3 | 0.365 | 0.433 | 0.506 | 0.587 | 0.774 | 0.978
| 51.7537 | C | 2321 | 1856 | 1547 | 1325 | 1159 | 1031 | 928 | 844 | 773 | 714 | 663 | 581 | 515
|  | D | 0.038 | 0.059 | 0.087 | 0.117 | 0.154 | 0.195 | 0.241 | 0.289 | 0.347 | 0.406 | 0.47 | 614 | 0.777
|  | U | 3151 | 2016 | 1401 | 1029 | 788 | 622 | 505 | 416 | 351 | 299 | 259 | 197 | 155
1-3/4"x3/16" | 12.2 | D | 0.042 | 0.064 | 0.092 | 0.126 | 0.165 | 0.208 | 0.258 | 0.31 | 0.371 | 0.435 | 0.506 | 0.664 | 0.838
| 59.5656 | C | 3151 | 2521 | 2100 | 1800 | 1575 | 1400 | 1260 | 1145 | 1049 | 969 | 899 | 786 | 700
|  | D | 0.033 | 0.052 | 0.074 | 0.101 | 0.132 | 0.167 | 0.206 | 0.249 | 0.297 | 0.347 | 0.403 | 0.527 | 0.667
|  | U | 4116 | 2633 | 1829 | 1344 | 1029 | 813 | 659 | 546 | 460 | 393 | 339 | 258 | 204
2"x3/16" | 13.9 | D | 0.036 | 0.056 | 0.081 | 0.111 | 0.144 | 0.183 | 0.226 | 0.273 | 0.325 | 0.384 | 0.447 | 0.58 | 0.732
| 67.8657 | C | 4116 | 3292 | 2745 | 2351 | 2058 | 1828 | 1646 | 1496 | 1370 | 1266 | 1175 | 1027 | 914
|  | D | 0.029 | 0.045 | 0.064 | 0.088 | 0.115 | 0.145 | 0.18 | 0.217 | 0.259 | 0.303 | 0.353 | 0.46 | 0.583
|  | U | 5209 | 3332 | 2314 | 1670 | 1302 | 1028 | 835 | 689 | 583 | 496 | 428 | 327 | 259
2-1/4"x3/16" | 15.4 | D | 0.032 | 0.05 | 0.072 | 0.098 | 0.127 | 0.162 | 0.199 | 0.241 | 0.287 | 0.338 | 0.393 | 0.512 | 0.646
| 75.1894 | C | 5209 | 4167 | 3473 | 2916 | 2604 | 2314 | 2082 | 1892 | 1733 | 1601 | 1487 | 1301 | 1157
|  | D | 0.026 | 0.039 | 0.057 | 0.079 | 0.102 | 0.129 | 0.16 | 0.194 | 0.23 | 0.27 | 0.314 | 0.41 | 0.518
|  | U | 6432 | 4115 | 2858 | 2099 | 1609 | 1271 | 1029 | 850 | 720 | 613 | 529 | 405 | 320
2-1/2"x3/16' | 17.1 | D | 0.028 | 0.044 | 0.064 | 0.088 | 0.116 | 0.145 | 0.18 | 0.217 | 0.26 | 0.305 | 0.354 | 0.465 | 0.586
| 83.4895 | C | 6432 | 5147 | 4286 | 3673 | 3214 | 2858 | 2571 | 2338 | 2141 | 1977 | 1836 | 1607 | 1429
|  | D | 0.023 | 0.036 | 0.051 | 0.071 | 0.092 | 0.116 | 0.144 | 0.173 | 0.207 | 0.242 | 0.282 | 0.369 | 0.467

## Bolts
Bolt Length w/ | [6 empty] | Bolt Length w/
Single Nut & Single Washer Calculator | [6 empty] | Single Nut & Single Washer Calculator
Enter Grip Inches | [6 empty] | Enter Grip millimeters
Bolt | Grip | 1-Lg. | 2-Lg. |  |  |  | Bolt | Grip | 1-Lg. | 2-Lg.
Dia. |  | Inches | Inches |  |  |  | Dia. |  | mm | mm
0.5 | 1.25 | 2.0938 | 2.25 | 0.84375 | 1 |  | 13 | 32 | 53.4312 | 57.4 | 21.4312 | 25.4
0.625 |  |  |  | 1.0312 | 1.1875 |  | 16 |  |  |  | 26.1937 | 30.1625
0.75 |  |  |  | 1.1562 | 1.3125 |  | 19 |  |  |  | 29.3687 | 33.3375
0.875 |  |  |  | 1.2812 | 1.4375 |  | 22 |  |  |  | 32.5437 | 36.5125
1 |  |  |  | 1.4062 | 1.5625 |  | 25 |  |  |  | 35.7188 | 39.6875
1.125 |  |  |  | 1.6562 | 1.8125 |  | 30 |  |  |  | 42.0687 | 46.0375
1.25 |  |  |  | 1.7812 | 1.9375 |  | 32 |  |  |  | 45.2437 | 49.2125
1.375 |  |  |  | 1.9062 | 2.0625 |  | 35 |  |  |  | 48.4187 | 52.3875
1.5 |  |  |  | 2.0312 | 2.1875 |  | 38 |  |  |  | 51.5938 | 55.5625
1-With F.W. | [6 empty] | 1-With F.W.
2-With Bevel Washer | [6 empty] | 2-With Bevel Washer
Bolt Length
In order to determine the required bolt length, the value in the table below should be added to the Grip (I.e., the total thickness of all connected
material, exclusive of washers) or enter the Grip in the Calculator above for single nut with washer. The values are generalized with due allowance
for manufacturing tolerances to provide for full thread engagement of heavy hex nut, when installed. For each hardened flat washer that is used
add 5/32-inch, and for each bevel washer add 5/16-inch. The length is determined by use of the table/calculator should be adjusted to the next 1/4-inch.
Specify thread length when using Double Nuts
Nominal | Single Nut |  | Double Nut |  |  |  | Double
Bolt | To determine required Bolt |  | To determine required Bolt |  |  |  | Nut
Size | Length Add to Grip |  | Length Add to Grip |  |  |  | Thread Length
Inches (mm) | Inches | millimeters | Inches | millimeters |  | millimeters | Inches | millimeters
1/2" (13) | 11/16" | 17.4625 | 1-3/16" |  |  | 30.1625 | 1-1/2" | 38.1
5/8" (16) | 7/8" | 22.225 | 1-1/2" |  |  | 38.1 | 1-7/8" | 47.625
3/4" (19) | 1" | 25 | 1-3/4" |  |  | 44.45 | 2-1/8" | 53.975
7/8" (22) | 1-1/8" | 28.575 | 2" |  |  | 50.8 | 2-3/8" | 60.325
1" (25) | 1-1/4" | 31.75 | 2-1/4" |  |  | 57.15 | 2-3/4" | 69.85
1-1/8" (29) | 1-1/2" | 38.1 | 2-5/8" |  |  | 66.675 | 3-1/8" | 79.375
1-1/4" (32) | 1-5/8" | 41.275 | 2-7/8" |  |  | 73.025 | 3-1/4" | 82.55
1-3/8" (35) | 1-3/4" | 44.45 | 3-1/8" |  |  | 79.375 | 3-5/8" | 92.075
1-1/2" (38) | 1-7/8" | 47.625 | 3-3/8" |  |  | 85.725 | 3-3/4" | 95.25
Bolted Parts (ASTM A325 & A490 BOLTS)
The slope of surfaces of bolted parts in contact with the bolt head and nut shall not exceed 1:20 with respect to plane normal to the bolt
axis. Bolted steel parts shall not be separated by gaskets and shall fit solidly together after bolts are tightened. Holes may be be punched,
sub-punched and reamed, or drilled, as required by applicable code or specification. Standard holes shall have a diameter 1/16" in excess of
the nominal bolt diameter.
A490 bolts and galvanized A325 bolts shall not be reused. Retightening previous tightening of adjacent bolts
shall not be considered as reuse.
Oversized Holes may have nominal diameters up to: 3/16" larger than bolts 7/8" and less in diameter, 1/4" for 1" in diameter
and 5/16" larger than bolts 1-1/8" and greater in diameter. Haredened washers shall be installed over oversized holes in an outer ply.
| Max. Holes Size (Nominal) Inches | [6 empty] | Max. Holes Size (Nominal) millimeters
Nominal | Oversize | Short | Long |  |  |  | Nominal | Oversize | Short | Long
Bolt | Holes | Slotted | Slotted |  |  |  | Bolt | Holes | Slotted | Slotted
Size |  | Holes | Holes |  |  |  | Size |  | Holes | Holes
1/2" | 5/8" | 9/16"x11/16" | 9/16"x1-1/4" |  |  |  | 13 | 16 | 14x17 | 14x32
5/8" | 13/16" | 11/16"x7/8" | 11/16"x1-9/16" |  |  |  | 16 | 21 | 17x22 | 17x40
3/4" | 15/16" | 13/16"x1" | 13/16"x1-7/8" |  |  |  | 19 | 24 | 21x25 | 21x48
7/8" | 1-1/16" | 15/16"x1-1/8" | 15/16"x2-3/16" |  |  |  | 22 | 27 | 24x29 | 24x56
1" | 1-1/4" | 1-1/16"x1-5/16" | 1-1/16"x2-1/2" |  |  |  | 25 | 32 | 27x33 | 27x64
1-1/8" | 1-7/16" | 1-3/16"x1-1/2" | 1-3/16"x2-13/16" |  |  |  | 29 | 37 | 30x38 | 30x71
1-1/4" | 1-9/16" | 1-5/16"x1-5/8" | 1-5/16"x3-1/8" |  |  |  | 32 | 40 | 33x41 | 33x79
1-3/8" | 1-11/16" | 1-7/16"x1-3/4" | 1-7/16"x3-7/16" |  |  |  | 35 | 43 | 37x44 | 37x87
1-1/2" | 1-13/16" | 1-9/16"x1-7/8" | 1-9/16"x3-3/4" |  |  |  | 38 | 46 | 40x58 | 40x95
>1-1/2" | d+5/16" | (d+1/16")x(d+3/8") | (d+1/16")x(2.5xd) |  |  |  | >38 | >46 | (d+2)x(d+9) | (d+2)x(2.5xd)
Minimum Bolt Spacing
The distance between centers of standard, oversized, or slotted fasteners shall be not less than 2 2/3d where "d" is the nominal
diameter of the fastener, inches. A distance of 3d is preferred.
Minimum Edge Distance Table Inches | [6 empty] | Minimum Edge Distance Table millimeters
(Center of Standard Hole to Edge of Connected Part) | [6 empty] | (Center of Standard Hole to Edge of Connected Part)
Nominal | @ | '@' Rolled Edges of |  |  |  |  | Nominal | @ | '@' Rolled Edges of
Bolt | Sheared | Plates, Shapes or Bars |  |  |  |  | Bolt | Sheared | Plates, Shapes or Bars
Size | Edges | or Gas Cut Edges |  |  |  |  | Size | Edges | or Gas Cut Edges
1/2" | 7/8" | 3/4" |  |  |  |  | 12.7 | 22.225 | 19.05
5/8" | 1-1/8" | 7/8" |  |  |  |  | 15.875 | 28.575 | 22.225
3/4" | 1-1/4" | 1" |  |  |  |  | 19.05 | 31.75 | 25
7/8" | 1-1/2" * | 1-1/8" |  |  |  |  | 22.225 | 38.1 | 28.575
1" | 1-3/4" * | 1-1/4" |  |  |  |  | 25 | 44.45 | 31.75
1-1/8" | 2" | 1-1/2" |  |  |  |  | 28.575 | 50.8 | 38.1
1-1/4" | 2-1/4" | 1-5/8" |  |  |  |  | 31.75 | 57.15 | 41.275
>1-1/4" | 1.75x Dia. | 1.25x Dia. |  |  |  |  | >32 | 1.75x Dia. | 1.25x Dia.
These may be 1-1/4" @ the ends of beam connection angles | [6 empty] | These may be 32 @ the ends of beam connection angles
Bolt
Size |  | Inches (mm) |  |  |  |  | Inches (mm)
Inches (mm) | A | B | C |  |  | A | B | C
1/4" (6) | 3/4" (19) | 1/2" (13) | 1/2" (13) |  |  | 1" (25) | 7/8" (22) | 5/8" (16)
3/8" (10) | 1-1/8" (29) | 3/4" (19) | 3/4" (19) |  |  | 1-3/8" (35) | 1-1/8" (29) | 3/4" (19)
1/2" (13) | 1-3/8" (35) | 7/8" (22) | 7/8" (22) |  |  | 1-3/4" (44) | 1-3/8" (35) | 7/8" (22)
5/8" (16) | 1-5/8" (41) | 1" (25) | 1" (25) |  |  | 2-1/8" (54) | 1-1/2" (38) | 1-1/8" (29)
3/4" (19) | 1-7/8" (48) | 1-1/8" (29) | 1-1/8" (29) |  |  | 2-5/8" (67) | 1-5/8" (41) | 1-1/4" (32)
7/8" (22) | 2-1/8" (54) | 1-1/4" (32) | 1-1/4" (32) |  |  | 3" (76) | 1-7/8" (48) | 1-5/8" (41)
1" (25) | 2-3/8" (60) | 1-3/8" (35) | 1-3/8" (35) |  |  | 3-1/4" (83) | 2-1/8" (54) | 1-7/8" (48)
1-1/8" (29) | 2-5/8" (67) | 1-1/2" (38) | 1-1/2" (38) |  |  | 3-3/8" (86) | 2-1/4" (57) | 1-7/8" (48)
1-1/4" (32) | 2-7/8" (73) | 1-5/8" (41) | 1-5/8" (41) |  |  | 3-7/8" (98) | 2-1/2" (64) | 2" (51)
1-3/8" (35) | 3-1/8" (79) | 1-3/4" (44) | 1-3/4" (44) |  |  | 4-3/8" (111) | 2-3/4" (70) | 2-1/4" (57)
1-1/2" (38) | 3-3/8" (86) | 1-7/8" (48) | 1-7/8" (48) |  |  | 4-7/8" (124) | 2-7/8" (73) | 2-1/2" (64)
| Bolt Dimensions. Inches |  |  |  |  | Nut Dimensions, Inches
Nominal | Heavy Hex Structural Bolts |  |  |  |  | Heavy Hex Nuts
Bolt Size | Width across | Height | Thread |  |  | Width across | Height
D | flats F | H | Length |  |  | flats W | H
1/2" (13) | 7/8" (22) | 5/16" (8) | 1" (25) |  |  | 7/8" (22) | 31/64" (12)
5/8" (16) | 1-1/16" (27) | 25/64" (10) | 1-1/4" (32) |  |  | 1-1/16" (27) | 39/64" (15)
3/4" (19) | 1-1/4" (32) | 15/32" (12) | 1-3/8" (35) |  |  | 1-1/4" (32) | 47/64" (19)
7/8" (22) | 1-7/16" (37) | 35/64" (14) | 1-1/2" (38) |  |  | 1-7/16" (37) | 55/64" (22)
1" (25) | 1-5/8" (41) | 39/64" (15) | 1-3/4" (44) |  |  | 1-5/8" (41) | 63/64" (25)
1-1/8" (29) | 1-13/16" (46) | 11/16" (17) | 2" (51) |  |  | 1-13/16" (46) | 1-7/64" (37)
1-1/4" (32) | 2" (51) | 25/32" (20) | 2" (51) |  |  | 2" (51) | 1-7/32" (31)
1-3/8" (35) | 2-3/16" (56) | 27/32" (21) | 2-1/4" (57) |  |  | 2-3/16" (56) | 1-11/32" (34)
1-1/2" (38) | 2-3/8" (60) | 15/16" (24) | 2-1/4" (57) |  |  | 2-3/8" (60) | 1-15/32" (37)
| Circular Washers | [5 empty] | Sq. or Rect. Bevel Washers
Nominal | Nominal | Nominal | Thickness |  |  |  | Minimum |  | Slope or
Bolt Size | Outside | Diameter |  |  |  |  | Side | Mean | Taper in
D | Diameter | of Hole | Min. |  |  | Max. | Dimension | Thickness | Thickness
1/2" (13) | 1-1/16" (27) | 17/32" (13) | 0.097 (2) |  |  | 0.177 (4) | 1-3/4" (44) | 5/16" (8) | 1:6'
5/8" (16) | 1-5/16" (33) | 11/16" (17) | 0.122 (3) |  |  | 0.177 (4) | 1-3/4" (44) | 5/16" (8) | 1:6'
3/4" (19) | 1-15/32" (37) | 13/16" (21) | 0.122 (3) |  |  | 0.177 (4) | 1-3/4" (44) | 5/16" (8) | 1:6'
7/8" (22) | 1-3/4" (44) | 15/16" (24) | 0.136 (3) |  |  | 0.177 (4) | 1-3/4" (44) | 5/16" (8) | 1:6'
1" (25) | 2" (51) | 1-1/8" (29) | 0.136 (3) |  |  | 0.177 (4) | 1-3/4" (44) | 5/16" (8) | 1:6'
1-1/8" (29) | 2-1/4" (57) | 1-1/4" (32) | 0.136 (3) |  |  | 0.177 (4) | 2-1/4" (57) | 5/16" (8) | 1:6'
1-1/4" (32) | 2-1/2" (64) | 1-3/8" (35) | 0.136 (3) |  |  | 0.177 (4) | 2-1/4" (57) | 5/16" (8) | 1:6'
1-3/8" (35) | 2-3/4" (70) | 1-1/2" (38) | 0.136 (3) |  |  | 0.177 (4) | 2-1/4" (57) | 5/16" (8) | 1:6'
1-1/2" (38) | 3" (76) | 1-5/8" (41) | 0.136 (3) |  |  | 0.177 (4) | 2-1/4" (57) | 5/16" (8) | 1:6'
Length |  |  | Weight of ASTM A325 or A490 high strength bolts
Under
Head |  |  | Heavy Hex Structural Bolts with Hex Nut in Pounds (Kg) per 100
Inches (mm) | 1/2" (13) | 5/8" (16) | 3/4" (19) |  |  | 7/8" (22) | 1" (25) | 1-1/8" (29) | 1-1/4" (32) | 1-3/8" (35) |  |  | 1-1/2" (38)
1" (25) | 16.5 (7.48) | 29.4 (13.34) | 47 (21.32)
1-1/4" (32) | 17.8 (8.07) | 31.1 (14.11) | 49.6 (22.5) |  |  | 74.4 (33.75) | 104 (47.17)
1-1/2" (38) | 19.2 (8.71) | 33.1 (15.01) | 52.2 (23.68) |  |  | 78 (35.38) | 109 (49.44) | 148 (67.13) | 197 (89.36)
1-3/4" (44) | 20.5 (9.29) | 35.3 (16.01) | 55.3 (25.08) |  |  | 81.9 (37.15) | 114 (51.71) | 154 (69.85) | 205 (92.99) | 261 (118.39) |  |  | 333 (151.05)
2" (51) | 21.9 (9.93) | 37.4 (16.96) | 58.4 (26.5) |  |  | 86.1 (39.05) | 119 (53.98) | 160 (72.57) | 212 (96.16) | 270 (122.47) |  |  | 344 (156.04)
2-1/4" (57) | 23.3 (10.57) | 39.8 (18.05) | 61.6 (27.94) |  |  | 90.3 (40.96) | 124 (56.25) | 167 (75.75) | 220 (99.79) | 279 (126.55) |  |  | 355 (161.03)
2-1/2" (64) | 24.7 (11.2) | 41.7 (18.91) | 64.7 (29.35) |  |  | 94.6 (42.91) | 130 (58.97) | 174 (78.93) | 229 (103.87) | 290 (131.54) |  |  | 366 (166.01)
2-3/4" (70) | 26.1 (11.84) | 43.9 (19.91) | 67.8 (30.75) |  |  | 98.8 (44.81) | 135 (61.23) | 181 (82.10) | 237 (107.50) | 300 (136.08) |  |  | 379 (171.91)
3" (76) | 27.4 (12.43) | 46.1 (20.91) | 70.9 (32.16) |  |  | 103 (46.72) | 141 (63.96) | 188 (85.28) | 246 (111.58) | 310 (140.61) |  |  | 391 (177.35)
3-1/4" (83) | 28.8 (13.06) | 48.2 (21.86) | 74 (33.57) |  |  | 107 (48.53) | 146 (66.22) | 195 (88.45) | 255 (115.67) | 321 (145.60) |  |  | 403 (182.80)
3-1/2" (89) | 30.2 (13.70) | 50.4 (22.86) | 77.1 (34.97) |  |  | 111 (50.35) | 151 (68.49) | 202 (91.63) | 263 (119.29) | 332 (150.59) |  |  | 416 (188.69)
3-3/4" (95) | 31.6 (14.33) | 52.5 (23.81) | 80.2 (36.38) |  |  | 116 (52.62) | 157 (71.21) | 209 (94.80) | 272 (123.38) | 342 (155.13) |  |  | 428 (194.14)
4" (102) | 33 (14.97) | 54.7 (24.81) | 83.3 (37.78) |  |  | 120 (54.43) | 162 (73.48) | 216 (97.98) | 280 (127.01) | 353 (160.12) |  |  | 441 (200.03)
4-1/4" (108) | 34.3 (15.56) | 56.9 (25.81) | 86.4 (39.19) |  |  | 124 (56.25) | 168 (76.2) | 223 (101.15) | 289 (131.09) | 363 (164.65) |  |  | 453 (205.48)
4-1/2" (114) | 35.7 (16.19) | 59 (26.76) | 89.5 (40.6) |  |  | 128 (58.06) | 173 (78.47) | 230 (104.33) | 298 (135.17) | 374 (169.64) |  |  | 465 (210.92)
4-3/4" (121) | 37.1 (16.83) | 61.2 (27.76) | 92.7 (42.05) |  |  | 133 (60.33) | 179 (81.19) | 237 (107.50) | 306 (138.80) | 384 (174.18) |  |  | 478 (216.82)
5" (127) | 38.5 (17.46) | 63.3 (28.71) | 95.8 (43.45) |  |  | 137 (62.14) | 184 (83.46) | 244 (110.68) | 315 (142.88) | 395 (179.17) |  |  | 490 (222.26)
5-1/4" (133) | 39.9 (18.10) | 65.5 (29.71) | 98.9 (44.86) |  |  | 141 (63.96) | 190 (86.18) | 251 (113.85) | 324 (146.96) | 405 (183.70) |  |  | 503 (228.16)
5-1/2" (140) | 41.2 (18.69) | 67.7 (30.71) | 102 (46.27) |  |  | 146 (66.22) | 196 (88.9) | 258 (117.03) | 332 (15.59) | 416 (188.69) |  |  | 515 (233.60)
5-3/4" (146) | 42.6 (19.32) | 69.8 (31.66) | 105 (47.63) |  |  | 150 (68.04) | 201 (91.17) | 265 (120.20) | 341 (154.68) | 426 (193.23) |  |  | 527 (239.04)
6" (152) | 44 (19.96) | 71.9 (32.61) | 108 (48.99) |  |  | 154 (69.85) | 207 (93.89) | 272 (123.38) | 349 (158.30 | 437 (198.22) |  |  | 540 (244.94)
Per inch
additional | 5.5 (2.49) | 8.6 (3.9) | 12.4 (5.62) |  |  | 16.9 (7.67) | 22.1 (10.02) | 28 (12.70) | 34.4 (15.60) | 42.5 (19.28) |  |  | 49.7 (22.54)
Add
For Each
100 F.W. | 2.1 (0.95) | 3.6 (1.63) | 4.8 (2.18) |  |  | 7 (3.18) | 9.4 (4.26) | 11.3 (5.13) | 13.8 (6.26) | 16.8 (7.62) |  |  | 20 (9.07)
Add
For Each
100
Bevel | 23.1 (10.48) | 22.4 (10.16) | 21 (9.53) |  |  | 20.2 (9.16) | 19.2 (8.71) | 34 (15.42) | 31.6 (14.33)
Washers
Add
Oversized and Slotted Holes
ASTM A325 & A490 BOLTS & NUTS
ASTM A325 & A490 BOLTS & NUTS DIMENSIONS,Inches (mm)
WASHER DIMENSIONS, Inches (mm)
F
Bolt Length
H
W
H
Adjust
Bolt
Length
to the
Next
1/4"
Adjust
Bolt
Length
to the
Next
6mm
Adjust
Bolt
Length
to the
Next
1/4"
or
6mm
c
B
A
Socket Wrench
Open End Wrench
Wrench Clearance Guide

## Girder wt
Girder - Formulas |  |  |  | Flg. Width "bf" | [5 empty] | Plate - Formulas
| 2017-06-13 14:31 |  |  |  |  | 10
[6 empty] | 450 |  |  |  | Pl Thk. | Pounds | Kilograms
| Flg. Thk "tf" | [8 empty] | Inches | per Sq. Ft | per Sq. Meter
| 0.75 | [8 empty] | 0.75 | 30.625 | 149.5244
| 25 | [8 empty] | KEY IN
[5 empty] | Web thk. "tw" |  |  |  |  | Pl Thk. | Pounds | Kilograms
|  | Depth | 48 |  | 0.375 |  |  | Web Inches | Web mm | mm | per Sq. Ft | per Sq. Meter
|  | "d" | 1200 |  | 10 |  |  | 46.5 | 1150 | 19.05 | 30.625 | 149.5244
KEY IN
English
| Depth | Web Thk. | Flg. Width | Flg. Thk. | Girder | Weight | Sq. Feet | Sq.Meters | Girder | Flg. Plates | Flg. Plates | Web. Plate | Web. Plate
| Inches | Inches | Inches | Inches | Weight | Weight | Surface Area | Surface Area | Length | Total | Total | Total | Total
| d | tw | bf | tf | lbs/ft | Kg/M | Per Ft | Per Meter | Feet | Sq. Ft | Sq. Meters | Sq. Ft | Sq. Meters
| 48 | 0.375 | 10 | 0.75 | 110.3776 | 164.26 | 11.2708 | 3.4354 | 10 | 16.6667 | 1.5484 | 38.75 | 3.6
| KEY IN | KEY IN | KEY IN | KEY IN | Lbs. | Kg |  |  | KEY IN | Lbs. | Kg | Lbs. | Kg
|  | Total Weight x Length |  |  | 1103.776 | 500.6644 |  | Total Weight |  | 510.4167 | 231.5211 | 593.3594 | 269.1433
Metric
| Depth | Web Thk. | Flg. Width | Flg. Thk. | Weight | Weight | Sq. Feet | Sq.Meters | Girder | Flg. Plates | Flg. Plates | Web. Plate | Web. Plate
| mm | mm | mm | mm |  |  | Surface Area | Surface Area | Length | Total | Total | Total | Total
| d | tw | bf | tf | lbs/ft | Kg/M | Per Ft | Per Meter | Meters | Sq. Feet | Sq. Meters | Sq. Feet | Sq. Meters
| 1200 | 10 | 450 | 25 | 179.3267 | 266.8676 | 13.7139 | 4.18 | 1 | 9.6875 | 0.9 | 12.3785 | 1.15
| KEY IN | KEY IN | KEY IN | KEY IN | Lbs. | Kg |  |  | KEY IN | Lbs. | Kg | Lbs. | Kg
|  | Total Weight x Length |  |  | 588.3423 | 266.8676 |  | Total Weight |  | 389.3442 | 176.6036 | 198.9981 | 90.264
Inches
Inches
mm
Inches
mm
mm
mm
Inches
Note on K5: Enter Plate Thickness in Inches
Note on K10: Enter Plate Thickness in Millimeters
Note on B18: Enter Girder Depth in Inches
Note on C18: Enter Web Thickness In Inches
Note on D18: Enter Flange Width in Inches
Note on E18: Enter Flange Thickness in Inches
Note on J18: Enter Girder Length in Feet
Note on B25: Enter Girder Depth in Millimeters
Note on C25: Enter Web Thickness in Millimeters
Note on D25: Enter Flange Width in Millimeters
Note on E25: Enter Flange Thickness in Millimeters
Note on J25: Enter Girder Length in Meters

## Weights
Structural Plate Weight (Metric) | [11 empty] | Qty. | Pl Thk. | Width | Length | Total | Weight | Weight | Pl Thk. | Pounds
Qty. | Pl Thk. | Width | Length | Total | Weight | Weight | Pl Thk. | Pounds | Kilograms |  |  |  | Inches | Inches | Inches | Sq. Ft | Lbs | Kg | Inches | per Sq. Ft
| mm | mm | mm | Sq. Meters | Kg | Lbs | mm | per Sq. Ft | per Sq. Meter |  |  | 1 | 0.5 | 6.5 | 12 | 0.54167 | 11.059 | 5.0163 | 0.5 | 20.4167
1 | 25.4 | 800 | 800 | 0.64 | 127.5941 | 281.2969 | 25.4 | 40.8333 | 199.3658 |  |  | Structural Plate Weight (English)
Key In | Key In | Key In | Key In | [8 empty] | Qty. | Pl Thk. | Width | Length | Total | Weight | Weight | Pl Thk. | Pounds
[13 empty] | Inches | Inches | Inches | Sq. Ft | Lbs | Kg | Inches | per Sq. Ft
Structural Plate Weight (English) | [11 empty] | 1 | 0.25 | 11.5 | 12 | 0.95833 | 9.783 | 4.4375 | 0.25 | 10.2083
Qty. | Pl Thk. | Width | Length | Total | Weight | Weight | Pl Thk. | Pounds | Kilograms
| Inches | Inches | Inches | Sq. Ft | Lbs | Kg | Inches | per Sq. Ft | per Sq. Meter
1 | 0.75 | 18 | 15 | 1.875 | 57.4219 | 26.0461 | 0.75 | 30.625 | 149.5244
Key In | Key In | Key In | Key In
Inches
| O.D. Inches |  |  |  |  | 6.5
| 22.25 |  |  |  |  | Key In
Key In
|  |  | Lbs/Ft. |  |  |  |  | Depth Inches |  |  | Depth Inches
|  |  | 227.1655 |  | Inches |  |  | 12.75 |  |  | 12
|  |  | Kg/Meter |  | 0.5 |  |  | Key In
|  |  | 338.0595 |  | Key In
Inches
[7 empty] | 12.75 |  |  |  | 0.25 | **Pipe - Formulas
[7 empty] | Key In |  |  |  | Key In | Pipe | Wall | Weight | Weight | Surface area | Wt. Of | Wt Of Pipe | Surface area
Wall Thk. Inches
|  | 1 |  |  | Lbs/Ft. | Kg/Meter | [5 empty] | O.D. | Thk. | Lbs/Ft | Kg/M | Sq.Ft-per Ft. | Water/Ft-Lbs. | & Water-Lbs/Ft | Sq. M-per M
|  | Key In |  |  | 20.842 | 31.0163 | [5 empty] | 22.25 | 1 | 227.1655 | 338.0595 | 5.825 | 139.5603 | 366.7259 | 1.7755 |  | 10.125 | 1095.9065
[12 empty] | ** Use Pipe Weights if Given Below | [8 empty] | 11.125 | 1323.072
227.1655
Steel Angle Properties - CG's & Lbs/Ft |  |  |  |  | Round Bar (dia in millimeters) - Lbs/Ft
Height = | 4 | inches |  |  | Diameter = | 12.7 | mm |  |  | mm
Width = | 6 | inches
[5 empty] | Lbs/Ft = | 0.668
Thickness = | 0.75 | inches |  |  | Kg/M = | 0.99409
Round Bar (dia in inches) - Lbs/Ft
Lbs/Ft = | 23.61
Kg/M = | 35.1356 |  |  |  | Diameter = | 0.5 | inches |  |  | inches
Xcg = | 2.08 | inches
Ycg = | 1.08 | inches |  |  | Lbs/Ft = | 0.668
[5 empty] | Kg/M = | 0.99409
Steel Plate Properties - Lbs/Ft |  |  |  |  | Conversions - Metric / U.S.
Width = | 12 | inches |  |  | pounds X 0.45359 = kilograms
Thickness = | 0.75 | inches |  |  | kilograms X 2.2046 = pounds
inches X 25.4 = millimeters
Lbs/Ft = | 30.63
millimeters X 0.03937 = inches
Steel Plate Properties - Lbs/Ft |  |  |  |  | feet X 0.3048 = meters
Width = | 305 | mm |  |  | meters X 3.28084 = feet
Thickness = | 3 | mm |  |  | cubic feet X 0.02832 = cubic meters
cubic meters X 35.3107 = cubic feet
Lbs/Ft = | 4.83
kilograms/meter X 0.6720 = pounds/foot
Steel Pipe Properties - Lbs/Ft |  |  |  |  | pounds/foot X 1.4881 = kilograms/meter
Outside Dia = | 12.75 | inches |  |  | Miscellaneous - Metric / U.S.
Wall Thck = | 0.5 | inches |  |  | Steel = 7850 kilograms per cubic meter
Steel = 490 pounds per cubic foot
Lbs/Ft = | 65.48
Kg/M = | 97.445
Steel Angle Properties - CG's & Kgs/M |  |  |  |  | Steel Tee Properties - CG's & Kgs/M
Height = | 102 | millimeters |  |  | Height = | 305 | millimeters |  |  | millimeters
Thickness = | 10 | millimeters |  |  | Thickness = | 10 | millimeters |  |  | millimeters
Width = | 102 | millimeters |  |  | Flange = | 102 | millimeters |  |  | millimeters
Thickness = | 10 | millimeters |  |  | Thickness = | 15 | millimeters |  |  | millimeters
Kg/M = | 15.23 |  |  |  | Kg/M = | 34.78
Xcg = | 29 | millimeters |  |  | Xcg = | 51 | millimeters |  |  | millimeters
Ycg = | 29 | millimeters |  |  | Ycg = | 107 | millimeters |  |  | millimeters
Steel Cone Weight (English Units - Inches) |  |  |  | Steel Cone Weight (Metric Units -millimeters) | [18 empty] | d1= | 12 | 144
[23 empty] | d2= | 10.25 | 105.0625
| 12 |  |  |  |  | 304.8 | [16 empty] | D1= | 36 | 1296
[23 empty] | D2= | 34.25 | 1173.0625
| 10.25 |  | 0.875 |  |  | 260.35 |  |  |  |  | 22.225 | [11 empty] | H= | 30 | 900
7.854
242.8125
|  |  | 30 | [7 empty] | 762 | [12 empty] | 1907.0494
|  |  | Inches | [7 empty] | millimeters | [12 empty] | 540.7721
[23 empty] | d1= | 12 | 144
[23 empty] | d2= | 10.25 | 105.0625
| 34.25 |  | 0.875 |  |  | 869.95 |  |  |  |  | 22.225 | [11 empty] | D1= | 36 | 1296
[23 empty] | D2= | 34.25 | 1173.0625
| 36 |  |  |  |  | 914.4 | [16 empty] | H= | 30 | 900
| Diameters |  |  |  |  | Diameters
| Inches |  |  |  |  | millimeters | [17 empty] | 7.854
242.8125
Lbs = | 540.7721 |  |  |  | Lbs = | 540.7721 | [17 empty] | 1907.0494
Kg = | 245.2901 |  |  |  | Kg = | 245.2901 | [17 empty] | 540.7721
Pipe Weight
Key In
Tee Weight
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In
Key In

## Brace Formulas
Brace Length w/ 2" Clr. (English)
2017-06-13 14:31
Inches |  |  |  |  | Feet
14.4483 |  |  |  |  | 10
[5 empty] | Key In |  |  |  |  | Brace Length
[10 empty] | Feet | Meters | 8.6927 | 75.5632
Inches | [9 empty] | 12.4853 | 3.8055 | 8.9792 | 80.6254
12.25 | [12 empty] | 156.1886
Key In | [12 empty] | 0.55208
[8 empty] | Inches |  |  |  |  | 0.3048
[5 empty] | 48.4606 |  |  | 10.625 |  |  |  |  | 155.8838
[8 empty] | Key In |  |  |  |  | 12.4853
Inches
[6 empty] | 6.625 |  |  |  | Feet |  |  | b | c |  | a | A | B | C
[6 empty] | Key In |  |  |  | 10 |  |  | 8.9792 | 8.6927 |  | 12.4975 | 90 | 45.9287 | 44.0713
[10 empty] | Key In |  |  | b | c |  | a | A | B | C
[13 empty] | 12.4853 | 0.55208 |  | 12.4975 | 90 | 87.4681 | 2.5319
| Inches |  |  | Feet | [8 empty] | b | C |  | a | A | c | B
| 12.75 |  |  | 12.4853 | [8 empty] | 3.3125 | 41.5394 |  | 4.4255 | 90 | 2.9347 | 48.4606
| Key In | [11 empty] | b | C |  | a | A | c | B
[13 empty] | 12.8005 | 48.4606 |  | 19.303 | 90 | 14.4483 | 41.5394
[8 empty] | Inches |  |  |  |  | b | C |  | a | A | c | B
[8 empty] | 13.249 |  |  |  |  | 11.738 | 48.4606 |  | 17.7008 | 90 | 13.249 | 41.5394
Brace Length W.P. to W.P (English)
Feet
| Inches |  |  |  | 25 | [8 empty] | 625 | 1.5833
| 5 |  |  |  | Key In | [7 empty] | 25.5833 | 654.5069
| Key In | [8 empty] | Brace Length |  |  |  | 1279.5069
|  |  |  | Inches | [5 empty] | Feet | Meters
|  |  |  | 18.5668 | [5 empty] | 33.1965 | 10.1183
Inches |  |  |  |  | Feet | [8 empty] | a= | 1.5833 | 0.53125
24 |  |  |  |  | 22.4756 | [8 empty] | A= | 25.5833
Key In | [13 empty] | B= | 25
[14 empty] | b= | 1.5472
Inches |  |  |  |  | 44.3393
9.6534 | [13 empty] | a1= | 0.53125 | 0.55173
[6 empty] | Inches | [7 empty] | b1= | 0.51914
[6 empty] | 12.75 |  |  |  | Feet |  |  |  | c1= | 0.74279
[6 empty] | Key In |  |  |  | 25 |  |  | b | c |  | a | A | B | C
[10 empty] | Key In |  |  | 22.4756 | 23 |  | 32.1582 | 90 | 44.3393 | 45.6607
| Feet | [5 empty] | Inches
| 23 |  |  | Feet |  |  | 11.7264
33.1965
Inches
2.813
[14 empty] | a2= | 12
[14 empty] | b2= | 0.9772
[9 empty] | Inches | [5 empty] | 23.9611 | 574.1362
[9 empty] | 12 | [5 empty] | 23 | 529
[9 empty] | Key In | [6 empty] | 1103.1362
[15 empty] | 1.0625 | 1.1289
1102.0073
33.1965
Brace Length W.P. to W.P (English)
Feet
| Inches |  |  |  | 6 | [8 empty] | 36 | 1.25
| 10 |  |  |  | Key In | [7 empty] | 24.1667 | 584.0278
| Key In | [8 empty] | Brace Length |  |  |  | 620.0278
|  |  |  | Inches | [5 empty] | Feet | Meters |  | b | c |  | a | A | B | C
|  |  |  | 3.7241 | [5 empty] | 24.0252 | 7.3229 |  | 22.9167 | 5.6897 |  | 23.6124 | 90 | 76.0568 | 13.9432
Inches |  |  |  |  | Feet
25 |  |  |  |  | 5.6897 | [8 empty] | A= | 24.1667 | 584.0278
Key In | [13 empty] | B= | 6 | 36
[14 empty] | C= | 24.9004 | 620.0278
Inches |  |  |  |  | 76.0568
-2.8444 | [13 empty] | a1= | 1.25 | 1.5625
[6 empty] | Inches | [7 empty] | b1= | 0.31034 | 0.096314
[6 empty] | 12.75 |  |  |  | Feet |  |  |  | c1= | 1.2879 | 1.6588
[6 empty] | Key In |  |  |  | 25
[8 empty] | Tubular |  | Key In |  |  |  | a2= | 0.53125 | 0.28223
| Feet | [6 empty] | Inches | [5 empty] | b2= | 0.1319 | 0.017397
| 22.9167 |  |  | Feet |  |  |  | 10.75 | [5 empty] | c2= | 0.54738 | 0.29962
|  |  |  | 24.0252 |  |  |  | Key In | [5 empty] | a3= | 1.8041 | 3.2548
[14 empty] | b3= | 0.44792 | 0.20063
[14 empty] | c3= | 1.8589 | 3.4554
[14 empty] | a4= | 2.1398 | 4.5786
[14 empty] | b4= | 0.53125 | 0.28223
[14 empty] | c4= | 2.2047 | 4.8608
|  |  | Inches | [10 empty] | 5.7891 | 33.5139
|  |  | -4.8073 | [10 empty] | 24.0252 | 577.2093
23.3173
0
0
Brace Length 1"Clr.to 2"Clr. (English)
Feet
10.5
Key In
Brace Length
[10 empty] | Feet | Meters
|  |  |  | Inches | [5 empty] | 13.4211 | 4.0907
Inches |  |  |  | 10.7319
20
Key In | [11 empty] | A= | 8.7917 | 77.2934
[12 empty] | B= | 10.1406 | 102.8323
[5 empty] | 40.9245 | [6 empty] | C= | 13.4211 | 180.1257
[6 empty] | Inches | [5 empty] | a1= | 0.53125 | 0.28223
[6 empty] | 12.75 |  |  |  | Feet |  | b1= | 0.61276 | 0.37548
[6 empty] | Key In |  |  |  | 10.625 |  | c1= | 0.81099 | 0.6577
[10 empty] | Key In |  |  | b | c |  | a | A | B | C
| Feet | [6 empty] | Inches |  |  |  |  | 10.1406 | 8.7917 |  | 13.4211 | 90 | 49.0755 | 40.9245
| 8.9583 |  |  | Feet |  |  |  | 6.625 |  |  |  |  | 8.7917
|  |  |  | 13.4211 |  |  |  | Key In |  |  |  |  | 10.1406
Brace Length w/ 50mm Clr. (Metric)
millimeters
3000
millimeters |  |  |  | millimeters | Key In
273 |  |  |  | -183.5747
Brace Length
[10 empty] | Feet | Meters | 2600 | 6760000
millimeters | [9 empty] | 8.6012 | 2.6217 | 454 | 206116
546 | [12 empty] | 6966116
Key In | [12 empty] | 305
[8 empty] | millimeters |  |  |  |  | 93025
[5 empty] | 16.5407 |  |  | 300 |  |  |  |  | 6873091
[8 empty] | Key In |  |  |  |  | 2621.6581
millimeters
[6 empty] | 305 |  |  |  | millimeters |  |  | b | c |  | a | A | B | C
[6 empty] | Key In |  |  |  | 1000 |  |  | 454 | 2600 |  | 2639.3401 | 90 | 9.9049 | 80.0951
[10 empty] | Key In |  |  | b | c |  | a | A | B | C
[13 empty] | 2621.6581 | 305 |  | 2639.3401 | 90 | 83.3641 | 6.6359
| millimeters |  |  | millimeters | [8 empty] | b | B |  | a | A | c | C
| 300 |  |  | 2621.6581 | [8 empty] | 273 | 16.5407 |  | 958.914 | 90 | 919.2318 | 73.4593
| Key In | [11 empty] | b | B |  | a | A | c | C
[13 empty] | 152.5 | 16.5407 |  | 535.6571 | 90 | 513.4903 | 73.4593
[13 empty] | b | B |  | a | A | c | C
[13 empty] | 857 | 16.5407 |  | 3010.2172 | 90 | 2885.647 | 73.4593
millimeters
|  | millimeters | [6 empty] | 130
|  | 260 | [5 empty] | millimeters
|  | Key In | [5 empty] | 297.9277
Brace Length w/ 2" Clr. (Metric)
FEET
10
Inches |  |  |  | Inches | Key In
4.1875 |  |  |  | 12.3825
Brace Length
[10 empty] | Feet | Meters | 104.625 | 10946.3906
Inches | [9 empty] | 9.2693 | 2.8253 | 39.625 | 1570.1406
8.375 | [12 empty] | 12516.5312
Key In | [12 empty] | 12
[8 empty] | Inches |  |  |  |  | 144
[5 empty] | 26.9008 |  |  | 12 |  |  |  |  | 12372.5312
[8 empty] | Key In |  |  |  |  | 9.2693
Inches
[6 empty] | 12 |  |  |  | FEET |  |  | b | c |  | a | A | B | C
[6 empty] | Key In |  |  |  | 4 |  |  | 39.625 | 104.625 |  | 111.8773 | 90 | 20.7434 | 69.2566
[10 empty] | Key In |  |  | b | c |  | a | A | B | C
[13 empty] | 111.2319 | 12 |  | 111.8773 | 90 | 83.8426 | 6.1574
| Inches |  |  | FEET | [8 empty] | b | B |  | a | A | c | C
| 10.75 |  |  | 9.2693 | [8 empty] | 4.1875 | 26.9008 |  | 9.2552 | 90 | 8.2537 | 63.0992
| Key In | [11 empty] | b | B |  | a | A | c | C
[13 empty] | 6 | 26.9008 |  | 13.2612 | 90 | 11.8263 | 63.0992
[13 empty] | b | B |  | a | A | c | C
[13 empty] | 47.125 | 26.9008 |  | 104.1559 | 90 | 92.8854 | 63.0992
Inches
|  | Inches | [6 empty] | 3.3125
|  | 6.625 | [5 empty] | Inches
|  | Key In | [5 empty] | 14.7322
2" clr.
2" clr.
W.P.
W.P.
W.P.
W.P.
1" Clr.
2" Clr.
50 clr.
50 clr.
Deg.
-
+
+
-
Deg.
Deg.
Deg.
Deg.
2" clr.
2" clr.
Deg.
-
+
+
-
Note on H4: Enter Length in Feet
Note on C8: Enter Depth in Inches
Note on L11: Enter Column Width Inches
Note on I14: Enter Brace Diameter Inches
Note on N15: Enter Depth in Feet
Note on D19: Enter Column Width Inches
Note on H34: Enter Length in Feet
Note on D35: Enter Offset in Inches
Note on C40: Enter Depth in Inches
Note on I46: Enter Brace Diameter Inches
Note on N47: Enter Depth in Feet
Note on D50: Warning !! Formula
Note on M59: Enter Offset in Inches
Note on H66: Enter Length in Feet
Note on D67: Enter Offset in Inches
Note on G70: Warning !! Formula
Note on C72: Enter Depth in Inches
Note on I78: Enter Brace Diameter Inches
Note on N79: Enter Depth in Feet
Note on L82: Enter Columun Width in Inches
Note on H99: Enter Length in Feet
Note on C105: Enter Depth in Inches
Note on I111: Enter Brace Diameter Inches
Note on N112: Enter Depth in Feet
Note on L115: Enter Columun Width in Inches

## Rt. Triang.
Right Triangle | [7 empty] | Converter
Feet + Inches = Total in Feet
[8 empty] | Feet | Inches | Total Feet | mm
[7 empty] | Key In | 8 | 9.25 | 8.7708 | 2673.35
Angles are in Degrees
Known
| Values Key in |  |  |  | Solutions
| a | b |  | c | A | B | C
Key In | 50 | 10 | Formulas | 48.9898 | 90 | 11.537 | 78.463
| a | c |  | b | A | B | C
Key In | 36 | 15 | Formulas | 32.7261 | 90 | 65.3757 | 24.6243
| a | B |  | b | A | c | C
Key In | 0 | 0 | Formulas | 0 | 90 | 0 | 90
| a | C |  | b | A | c | B
Key In | 0 | 0 | Formulas | 0 | 90 | 0 | 90
| b | c |  | a | A | B | C
Key In | 350 | 700 | Formulas | 782.6238 | 90 | 26.5651 | 63.4349
| b | B |  | a | A | c | C
Key In | 10 | 63.4349 | Formulas | 11.1803 | 90 | 5 | 26.5651
| b | C |  | a | A | c | B
Key In | 10 | 26.5651 | Formulas | 11.1803 | 90 | 5 | 63.4349
| c | C |  | a | A | b | B
Key In | 5 | 26.5651 | Formulas | 11.1803 | 90 | 10 | 63.4349
| c | B |  | a | A | b | C
Key In | 5 | 63.4349 | Formulas | 11.1803 | 90 | 10 | 26.5651
b
a
A=90
C
B
c

## Oblique Triang.
Converter
Feet + Inches = Total in Feet
Oblique Triangles | [7 empty] | Feet | Inches | Total Feet | mm
Angles are in Degrees | [6 empty] | Key In | 12 | 10.75 | 12.8958 | 3930.65
[8 empty] | Key In | Key In
Known
| Values Key in |  |  |  | Solutions
| a | B | A |  | C | b | c
Key In | 119.3125 | 42.6088 | 97.7487 | Formulas | 39.6425 | 81.5176 | 76.8223
| a | A | C |  | B | b | c
Key In | 119.3125 | 97.7487 | 39.6425 | Formulas | 42.6088 | 81.5176 | 76.8223
| a | A | b |  | B | C | c
Key In | 119.3125 | 97.7487 | 81.5175 | Formulas | 42.6087 | 39.6426 | 76.8224
| a | C | b |  | A | B | c
Key In | 119.3125 | 39.6425 | 81.5175 | Formulas | FALSE | FALSE | #DIV/0! | FALSE |  |  |  | -82.2512 | FALSE
[5 empty] | 97.7488 | 42.6087 | 76.8223 | Use this Line |  |  |  | 97.7488 | 42.6087
| a | b | c |  | A | B | C
Key In | 119.3125 | 83.3374 | 156.8052 | Formulas | 48.5596 | 31.5748 | 99.8656
| b | C | B |  | A | c | a
Key In | 81.5175 | 39.6425 | 42.6088 | Formulas | 97.7487 | 76.8222 | 119.3124
c
a
b
A
C
B

## Adding Calculator
English | [5 empty] | Metric |  | Password : ABB
|  | Total | Total |  |  | Total
|  | Millimeters | Meters |  |  | Millimeters
Feet | Inches | [5 empty] | Feet | Inches
Key in Feet & Inches Below | [5 empty] | Key in Millimeters Below
Feet | Inches | Millimeters | Meters |  | 0 | Millimeters | Feet | Inches |  | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
|  |  |  | 0 | 0 |  |  |  | 0 | 0
Total
Total

## Ladders
Fixed Ladder Design Notes:
Note:Use Client Standards if project required
See Standards for member sizes & additional details | 1. The minimum design live load shall be a single concentrated
load of 200 pounds (91Kg).
2. The number and position of additional concentrated live-load units
of 200 pounds (91 Kg) each as determined from anticipated usage of ladder
shall be considered in the design.
3. All ladders 20 Feet (6096mm) or more in length shall be equipped with safety cage.
Cages shall also be required where the ladder face is within 4'-0" (1219mm)
of an elevated platform edge.
4. Where ladder face is within 4'-0" (1219mm) of platform edge extend vertical cage
bars to platform handrail.
5. The side access ladder is the preferred to the step through (Front) access style.
6. All fixed ladders serving elevations 2'-6" (762mm) or more above ground, platform
or floor level shall be equipped with drop bar or safety gate attached as follows:
* Side access ladders hinged at ladder side with drop bar.
* Side access ladders opens at ladder side with safety gate.
7. The distance between rungs shall not exceed 12 inches (305mm) and shall
shall be uniformed throughout the length of the ladder. Any Spacing adjustments
to be at bottom rung to landing.
8. The maximum distance between landings shall not exceed 30'-0" (9144mm).
9. All rungs shall have a minimum diameter of 3/4" (20mm) except ladders formed
by individual metal rungs imbedded in concrete use a 1"(25mm) diameter bar minimum.
10. The minimum clear length of rungs shall be 16 inches (406mm).
11. On fixed ladders, the perpendicular distance from the center line of rungs to the
nearest permanent object on the climbing side of the ladder shall be 36 inches (914mm)
for a pitch of 76 degrees and 30 inches (762mm) for a pitch of 90 degrees.
12. A clear width of at least 15 inches (381mm) shall be provided each way from the
center line of the ladder in the climbing space.
13. The distance from the center line of rungs to the nearest permanent object in back
of the ladder shall not be less than 7 inches (178mm) except that when unavoidable
obstructions are encountered - See Detail Clearance for Unavoidable Obstruction
at rear of ladder (Below).
| 14. The step-across distance from the nearest edge of ladder to the nearest edge of | 2-1/2 inches (64mm)
landing shall not be more than 12 inches (305mm) or less than 2-1/2 Inches (64mm)
for front access ladders.
15. When ladders are used to ascend to heights exceeding 20 Feet (6096mm) landings
platforms shall be provided for each 30 Feet (9144mm) or fraction thereof, except
that, where no cage or ladder safety device is provided, landing platforms shall be
provided for each 20 Feet (6096mm) of height or fraction thereof.
16. Cages shall extend a minimum of 3'-6" (1067mm) above the top of landing,
unless other acceptable protection is provided.
17. Bottom Cages shall extend down the ladder to a point not less than 7 Feet (2134mm)
nor more than 8 Feet (2438mm) above the base of the ladder or landing.
18. Set top of rung flush with top of landing walking surface
19. Cages shall not extend less than 27" (686mm) nor more than 28" (711mm) from the
centerline of rungs of the ladder. Vertical bar spacing shall be located at a maximum
spacing of 40 degrees around the circumference of the cage - aprox. 9-1/2" (241mm) c/c
Smooth Wall
2'-3"
(686mm)
1'-3" Min.
(381mm)
See
Note12
1'-3" Min.
(381mm)
See
Note12
2'-6"
(762mm)
See Note11
Other Obstructions
7" Min.
(178mm)
See Note13
Clearance Diagram for Fixed Ladder in Well
Plan View
Fixed Ladder
12"Max.
(305mm)
20'-0" (6096mm) MAX.
[30'-0" (9144mm) with Cage]
See Notes 8 & 15
4'-0" Min.
(1219mm)
1'-3" Clr. Min.
(381mm) See Note 12
12" Max
(305mm)
See Note 7
Side Step Ladder
Top of Rung &
Top of Landing
Offset Fixed Ladder Sections
Front Elevation
1-1/2" MIN.
(38mm)
4-1/2" MIN.
(114mm)
Clearance for Unavoidable Obstruction
at Rear of Ladder
See Note 13
12" Max. (305mm)
2-1/2" Min. (64mm)
See Note 14
See Note4
7'-0" (2134mm) MIN.
8'-0" (2438mm) Max.
See Note 17
4'-0" (1219mm)
MAX. Spa.
2'-6" MIN.
(762mm)
3'-6" (1067mm) MIN.
See Note16
Top of Rung
& Landing
"X" Spaces @ 1'-0" (305mm) MAX. = X'-XX" (See Note 7)
("X" RUNGS)
Odd Spacing Should Always Occur at Bottom
30'-0" (9144mm) MAX.
See Note 15
7" Min. Clr.
(178mm)
See Note 13
Cages for Ladders More Than 20'-0" (6096mm)
16" (407mm) MIN
See Note 10
Ladder Supt.
(Typ.)

## Stairs
Stair Design Notes
1. Fixed stairs stringer size Should be determined as follows (unless specified by engineer) :
| Horizontal Run |  |  | Stringer
| Work Point to Work Point |  |  | Size
| Less Than 10 Feet (3048mm) |  |  | C8 or C10
| 10 to 20 Feet (3048 to 6096mm) |  |  | C10X15.3 Min.
| 20 Feet (6096mm) or More |  |  | C12 Min.
2. Sway Bracing should be provided on all stairs with horizontal work point to work point
of 15 Feet (4572mm) or more and all stairs with fiberglass treads.
3. Stair angles greater than 45 degrees should always be avoided if possible.
4. Stringer back to back dimension is typically 3'-0" (914mm) unless otherwise specified.
5. Any uniform combination of rise/tread dimensions may be used that will result in a stairway at the angle to
horizontal within the permissible range. The table below gives rise/tread dimensions which will produce a stairway
within the permissible range, stating the angle to the horizontal produced by each combination. However, the
rise/tread combination are not limited to those given in the table below. Odd tread spacing should always occur at the bottom step
| Angle | Rise | Tread |  |  | Feet + Inches = Total in Feet
| To |  |  |  |  | Feet | Inches | Total Feet | mm
| Horz. | Inches (mm) | Inches (mm) |  | Key In | 8 | 6 | 8.5 | 2590.8
| 30.58 | 6-1/2" (165) | 11" (279) |  | Note
| 32 | 6-3/4" (172) | 10-3/4" (273) |  | The addition of riser plus tread equals 17-1/2" (444mm)
| 33.68 | 7" (178) | 10-1/2" (267)
| 35.27 | 7-1/4" (184) | 10-1/4" (260) |  |  |  | Length WP to WP
| 36.87 | 7-1/2" (190) | 10" (254) |  | Angle Degrees |  | 107.4802
| 38.48 | 7-3/4" (197) | 9-3/4" (248) |  | 45
| 40 | 8" (203) | 9-1/2" (241) | [5 empty] | Key In | b | c |  | a | A | B | C
| 41.73 | 8-1/4" (210) | 9-1/4" (235) | [5 empty] | 76 | 76 | 76 | Formulas | 107.4802 | 90 | 45 | 45
| 43.37 | 8-1/2" (216) | 9" (229)
| 45 | 8-3/4" (222) | 8-3/4" (222)
| 46.63 | 9" (229) | 8-1/2" (216)
| 48 | 9-1/4" (235) | 8-1/4" (210) |  |  |  | Key In
| 49.9 | 9-1/2" (241) | 8" (203) |  |  |  | 76
6. Vertical clearance above any stair to an overhead obstruction shall be at least 7 FEET (2134mm) measured
from the leading edge of the tread.

## Vessel Platf.
2017-06-13 14:31
Vertical Vessel Platform Max. Bracket Spacing
6'-0" Max. C/C Brkt. On O.S. Rad./Edge
1829mm
2'-0" Max. Cantilever on O.S. Rad./Edge
610mm
| Key In Radius |  |  | 1'-5" CL Ladder to Platform on O.S. Rad.
Inches |  |  |  | 432mm
mm |  |  |  | O.S. Radius of Vessel plus Insulation (Key In)
Platform Width (Key In)
Clearance between vessel & platform - 3" min-4" Max. (Key in)
| Key In Clr. |  |  |  | 76mm to 102mm
Inches |  |  | Key In Platf. Width
mm |  |  |  | Inches |  | 0
|  |  |  | mm |  | 0
[6 empty] | b | c | a | A | B | C
[6 empty] | 0 | 36 | 36 | 90 | 0 | #DIV/0!
|  |  | Max. Brkt. Spa. |  |  | b | c | a | A | B | C
|  |  |  | Degrees |  | 0 | 914.4 | 914.4 | 90 | 0 | #DIV/0!
Degrees
Max. Brkt. Spa.
Degrees
Degrees
1
2
2
1
2
3
2
2
3
4
2
4
2
5
2
6
2
2
2
1
1
2
3
4
2
5
2
6
2
6
2
6
2
5
2
5
2
C8x11.5
C8x11.5
8"
200mm
Typical Hot Vessel Bracket Detail
4"
100mm
3-1/2" 89mm
5" 127mm
3-1/2" 89mm
2" 51mm
Vessel Clip Pl 1/2" (13mm)
& Dblr. Pl 1/2"x 6"X1'-4"
(13x150x406mm)
Top of Brkt. & Clip
Clip Ref. Elev.
4-13/16"Dia. Holes for 3/4"Dia. Bolt
4-21mm Dia. Holes for 19mm Dia. Bolt
ASTM A325N Bolts w/ L.I.W.
1-1/2" 38mm

## Pipe Tables
**Pipe - Formulas | [12 empty] | **Pipe - Formulas
Pipe | Wall | Weight | Weight | Surface | Wt. of Water | Wt of Pipe | Surface | Section Modulus = |  | 7.9168 |  |  | Pipe | Wall | Weight | Weight | Surface area | Wt. Of | Wt Of Pipe | Surface area
Inches | Inches |  |  | Area |  |  | Area | Moment of Inertia = |  | 39.5841
O.D. | Thk. | Lbs/Ft | Kg/M | Sq.Ft-per Ft. | per Ft - Lbs. | & Water-Lbs/Ft | Sq. M-per M | Raduis of Gyration= |  | 3.499 |  |  | O.D. | Thk. | Lbs/Ft | Kg/M | Sq.Ft-per Ft. | Water/Ft-Lbs. | & Water-Lbs/Ft | Sq. M-per M |  |  |  |  | Area
10 | 0.104 | 11.0021 | 16.373 | 2.618 | 32.6328 | 43.635 | 0.79796 | [5 empty] | 10 | 0.104 | 11.0021 | 16.373 | 2.618 | 32.6328 | 43.635 | 0.79796 |  | 9.792 | 4.896 | 256.2514 | 3.2333
KEY IN | KEY IN | [11 empty] | ** Use Pipe Weights if Given Below | [8 empty] | 95.8833 | 5 | 267.2535
Pipe Tables |  |  | ** Use Pipe Weights if Given Below | [18 empty] | 195.8833 |  | 11.0021
13.9958
Nominal | Outside | Desig- | Wall | Weight | Weight |  | Nominal | Outside | Desig- | Wall | Weight | Weight | [8 empty] | R | 3.499 |  | 11.0021
Pipe Size | Dia. | nation | Thickness | Lbs/ Ft. | Kg/M |  | Pipe Size | Dia. | nation | Thickness | Lbs/ Ft. | Kg/M
0.125 | 0.405 | 10S | 0.049 | 0.186 | 0.2768 |  | 14 | 14 | 10 Ga. | 0.134 | 20 | 29.7633
0.125 | 0.405 | Std. | 0.068 | 0.244 | 0.36311 |  | 14 | 14 | 8 Ga. | 0.164 | 24 | 35.7159
0.125 | 0.405 | X-Stg. | 0.095 | 0.314 | 0.46728 |  | 14 | 14 | 6 Ga. | 0.194 | 29 | 43.1568
[7 empty] | 14 | 14 | API | 0.21 | 31 | 46.1331
0.25 | 0.54 | 10S | 0.065 | 0.33 | 0.49109 |  | 14 | 14 | API | 0.219 | 32 | 47.6212
0.25 | 0.54 | Std. | 0.088 | 0.424 | 0.63098 |  | 14 | 14 | 3 Ga. | 0.239 | 35 | 52.0857
0.25 | 0.54 | X-Stg. | 0.119 | 0.535 | 0.79617 |  | 14 | 14 | 10 | 0.25 | 37 | 55.0621
[7 empty] | 14 | 14 | API | 0.281 | 41 | 61.0147
0.375 | 0.675 | 10S | 0.065 | 0.423 | 0.62949 |  | 14 | 14 | 20 | 0.312 | 46 | 68.4555
0.375 | 0.675 | Std. | 0.091 | 0.567 | 0.84379 |  | 14 | 14 | API | 0.344 | 50 | 74.4082
0.375 | 0.675 | X-Stg. | 0.126 | 0.738 | 1.0983 |  | 14 | 14 | Std. | 0.375 | 55 | 81.849
[7 empty] | 14 | 14 | 40 | 0.438 | 63 | 93.7543
0.5 | 0.84 | 10S | 0.083 | 0.671 | 0.99856 |  | 14 | 14 | X-Stg. | 0.5 | 72 | 107.1478
0.5 | 0.84 | Std. | 0.109 | 0.85 | 1.2649 |  | 14 | 14 | 60 | 0.594 | 85 | 126.4939
0.5 | 0.84 | X-Stg. | 0.147 | 1.087 | 1.6176 |  | 14 | 14 | -- | 0.625 | 89 | 132.4466
0.5 | 0.84 | 160 | 0.138 | 1.31 | 1.9495 |  | 14 | 14 | 80 | 0.75 | 107 | 159.2336
0.5 | 0.84 | XX-Stg. | 0.294 | 1.714 | 2.5507 |  | 14 | 14 | -- | 0.875 | 123 | 183.0442
[7 empty] | 14 | 14 | 100 | 0.938 | 131 | 194.9495
0.75 | 1.05 | 10S | 0.083 | 0.857 | 1.2754 |  | 14 | 14 | -- | 1 | 139 | 206.8548
0.75 | 1.05 | Std. | 0.113 | 1.13 | 1.6816 |  | 14 | 14 | 120 | 1.094 | 151 | 224.7128
0.75 | 1.05 | X-Stg. | 0.154 | 1.473 | 2.1921 |  | 14 | 14 | -- | 1.125 | 155 | 230.6654
0.75 | 1.05 | 160 | 0.219 | 1.94 | 2.887 |  | 14 | 14 | 140 | 1.25 | 171 | 254.4761
0.75 | 1.05 | XX-Stg. | 0.308 | 2.44 | 3.6311 |  | 14 | 14 | -- | 1.375 | 186 | 276.7985
[7 empty] | 14 | 14 | 160 | 1.406 | 190 | 282.7512
1 | 1.315 | 10S | 0.109 | 1.404 | 2.0894 |  | 14 | 14 | -- | 1.5 | 200 | 297.6328
1 | 1.315 | Std. | 0.133 | 1.678 | 2.4971
1 | 1.315 | X-Stg. | 0.179 | 2.171 | 3.2308 |  | 16 | 16 | 10 Ga. | 0.134 | 23 | 34.2278
1 | 1.315 | 160 | 0.25 | 2.85 | 4.2413 |  | 16 | 16 | 8 Ga. | 0.164 | 28 | 41.6686
1 | 1.315 | XX-Stg. | 0.358 | 3.659 | 5.4452 |  | 16 | 16 | -- | 0.188 | 32 | 47.6212
[7 empty] | 16 | 16 | 6 Ga. | 0.194 | 33 | 49.1094
1.25 | 1.66 | 10S | 0.109 | 1.806 | 2.6876 |  | 16 | 16 | API | 0.219 | 37 | 55.0621
1.25 | 1.66 | Std. | 0.14 | 2.272 | 3.3811 |  | 16 | 16 | 3 Ga. | 0.239 | 40 | 59.5266
1.25 | 1.66 | - | 0.191 | 2.996 | 4.4585 |  | 16 | 16 | 10 | 0.25 | 42 | 62.5029
1.25 | 1.66 | - | 0.25 | 3.764 | 5.6014 |  | 16 | 16 | API | 0.281 | 47 | 69.9437
1.25 | 1.66 | - | 0.382 | 5.214 | 7.7593 |  | 16 | 16 | 20 | 0.312 | 52 | 77.3845
[7 empty] | 16 | 16 | API | 0.344 | 57 | 84.8254
1.5 | 1.9 | 10S | 0.109 | 2.085 | 3.1028 |  | 16 | 16 | Std. | 0.375 | 63 | 93.7543
1.5 | 1.9 | Std. | 0.145 | 2.717 | 4.0433 |  | 16 | 16 | API | 0.438 | 73 | 108.636
1.5 | 1.9 | X-Stg. | 0.2 | 3.631 | 5.4035 |  | 16 | 16 | X-Stg. | 0.5 | 83 | 123.5176
1.5 | 1.9 | 160 | 0.281 | 4.862 | 7.2355 |  | 16 | 16 | -- | 0.625 | 103 | 153.2809
1.5 | 1.9 | XX-Stg. | 0.4 | 6.408 | 9.5362 |  | 16 | 16 | 60 | 0.656 | 108 | 160.7217
[7 empty] | 16 | 16 | -- | 0.75 | 122 | 181.556
2 | 2.375 | 10S | 0.109 | 2.638 | 3.9258 |  | 16 | 16 | 80 | 0.844 | 137 | 203.8785
2 | 2.375 | Std. | 0.154 | 3.652 | 5.4348 |  | 16 | 16 | -- | 0.875 | 141 | 209.8311
2 | 2.375 | X-Stg. | 0.218 | 5.022 | 7.4736 |  | 16 | 16 | -- | 1 | 160 | 238.1062
2 | 2.375 | - | 0.25 | 5.673 | 8.4424 |  | 16 | 16 | 100 | 1.031 | 165 | 245.5471
2 | 2.375 | 160 | 0.344 | 7.45 | 11.0868 |  | 16 | 16 | -- | 1.125 | 179 | 266.3814
2 | 2.375 | XX-Stg. | 0.436 | 9.029 | 13.4366 |  | 16 | 16 | 120 | 1.219 | 193 | 287.2157
[7 empty] | 16 | 16 | -- | 1.25 | 197 | 293.1683
2.5 | 2.875 | 10S | 0.12 | 3.53 | 5.2532 |  | 16 | 16 | -- | 1.375 | 215 | 319.9553
2.5 | 2.875 | Std. | 0.203 | 5.79 | 8.6165 |  | 16 | 16 | 140 | 1.438 | 224 | 333.3487
2.5 | 2.875 | X-Stg. | 0.276 | 7.66 | 11.3993 |  | 16 | 16 | -- | 1.5 | 232 | 345.2541
2.5 | 2.875 | 160 | 0.375 | 10.01 | 14.8965 |  | 16 | 16 | 160 | 1.594 | 245 | 364.6002
2.5 | 2.875 | XX-Stg. | 0.552 | 13.69 | 20.373
[7 empty] | 18 | 18 | 10 Ga. | 0.134 | 26 | 38.6923
3 | 3.5 | 10S | 0.12 | 4.33 | 6.4438 |  | 18 | 18 | 8 Ga. | 0.164 | 31 | 46.1331
3 | 3.5 | API | 0.125 | 4.52 | 6.7265 |  | 18 | 18 | 6 Ga. | 0.194 | 37 | 55.0621
3 | 3.5 | API | 0.156 | 5.58 | 8.304 |  | 18 | 18 | 3 Ga. | 0.239 | 45 | 66.9674
3 | 3.5 | API | 0.188 | 6.65 | 9.8963 |  | 18 | 18 | 10 | 0.25 | 47 | 69.9437
3 | 3.5 | Std. | 0.216 | 7.57 | 11.2654 |  | 18 | 18 | API | 0.281 | 49 | 72.92
3 | 3.5 | API | 0.25 | 8.68 | 12.9173 |  | 18 | 18 | 20 | 0.312 | 59 | 87.8017
3 | 3.5 | API | 0.281 | 9.65 | 14.3608 |  | 18 | 18 | API | 0.344 | 65 | 96.7307
3 | 3.5 | X-Stg. | 0.3 | 10.25 | 15.2537 |  | 18 | 18 | Std. | 0.375 | 71 | 105.6596
3 | 3.5 | 160 | 0.438 | 14.32 | 21.3105 |  | 18 | 18 | API | 0.406 | 76 | 113.1005
3 | 3.5 | XX-Stg. | 0.6 | 18.58 | 27.6501 |  | 18 | 18 | 30 | 0.438 | 82 | 122.0295
[7 empty] | 18 | 18 | X-Stg. | 0.5 | 93 | 138.3993
3.5 | 4 | 10S | 0.12 | 4.97 | 7.3962 |  | 18 | 18 | 40 | 0.562 | 105 | 156.2572
3.5 | 4 | API | 0.125 | 5.18 | 7.7087 |  | 18 | 18 | -- | 0.625 | 116 | 172.627
3.5 | 4 | API | 0.156 | 6.41 | 9.5391 |  | 18 | 18 | 60 | 0.75 | 138 | 205.3666
3.5 | 4 | API | 0.188 | 7.71 | 11.4737 |  | 18 | 18 | -- | 0.875 | 160 | 238.1062
3.5 | 4 | Std. | 0.226 | 9.11 | 13.5572 |  | 18 | 18 | 80 | 0.938 | 171 | 254.4761
3.5 | 4 | API | 0.25 | 10.02 | 14.9114 |  | 18 | 18 | -- | 1 | 182 | 270.8459
3.5 | 4 | API | 0.281 | 11.17 | 16.6228 |  | 18 | 18 | -- | 1.125 | 203 | 302.0973
3.5 | 4 | X-Stg. | 0.318 | 12.51 | 18.6169 |  | 18 | 18 | 100 | 1.156 | 208 | 309.5381
3.5 | 4 | XX-Stg. | 0.636 | 22.85 | 34.0045 |  | 18 | 18 | -- | 1.25 | 224 | 333.3487
[7 empty] | 18 | 18 | 120 | 1.375 | 244 | 363.112
4 | 4.5 | 10S | 0.12 | 5.61 | 8.3486 |  | 18 | 18 | -- | 1.5 | 265 | 394.3635
4 | 4.5 | API | 0.125 | 5.84 | 8.6909 |  | 18 | 18 | 140 | 1.562 | 275 | 409.2451
4 | 4.5 | API | 0.156 | 7.24 | 10.7743 |  | 18 | 18 | 160 | 1.781 | 309 | 459.8427
4 | 4.5 | API | 0.188 | 8.56 | 12.7387
4 | 4.5 | API | 0.219 | 10.02 | 14.9114 |  | 20 | 20 | 10 Ga. | 0.134 | 28 | 41.6686
4 | 4.5 | Std. | 0.237 | 10.79 | 16.0573 |  | 20 | 20 | 8 Ga. | 0.164 | 35 | 52.0857
4 | 4.5 | API | 0.25 | 11.35 | 16.8907 |  | 20 | 20 | 6 Ga. | 0.194 | 41 | 61.0147
4 | 4.5 | API | 0.281 | 12.67 | 18.855 |  | 20 | 20 | 3 Ga. | 0.239 | 50 | 74.4082
4 | 4.5 | API | 0.312 | 14 | 20.8343 |  | 20 | 20 | 10 | 0.25 | 53 | 78.8727
4 | 4.5 | X-Stg. | 0.337 | 14.98 | 22.2927 |  | 20 | 20 | API | 0.281 | 59 | 87.8017
4 | 4.5 | 120 | 0.438 | 19 | 28.2751 |  | 20 | 20 | API | 0.312 | 66 | 98.2188
4 | 4.5 | -- | 0.5 | 21.36 | 31.7872 |  | 20 | 20 | API | 0.344 | 72 | 107.1478
4 | 4.5 | 160 | 0.531 | 22.6 | 33.6325 |  | 20 | 20 | Std. | 0.375 | 79 | 117.565
4 | 4.5 | XX-Stg. | 0.674 | 27.54 | 40.984 |  | 20 | 20 | API | 0.406 | 85 | 126.4939
[7 empty] | 20 | 20 | API | 0.438 | 92 | 136.9111
5 | 5.563 | 10S | 0.134 | 7.77 | 11.563 |  | 20 | 20 | X-Stg. | 0.5 | 105 | 156.2572
5 | 5.563 | API | 0.156 | 9.02 | 13.4232 |  | 20 | 20 | 40 | 0.594 | 123 | 183.0442
5 | 5.563 | API | 0.188 | 10.8 | 16.0722 |  | 20 | 20 | -- | 0.625 | 129 | 191.9732
5 | 5.563 | API | 0.219 | 12.51 | 18.6169 |  | 20 | 20 | 60 | 0.812 | 167 | 248.5234
5 | 5.563 | Std. | 0.258 | 14.62 | 21.757 |  | 20 | 20 | -- | 0.875 | 179 | 266.3814
5 | 5.563 | API | 0.281 | 15.86 | 23.6023 |  | 20 | 20 | -- | 1 | 203 | 302.0973
5 | 5.563 | API | 0.312 | 17.51 | 26.0578 |  | 20 | 20 | 80 | 1.031 | 209 | 311.0263
5 | 5.563 | API | 0.344 | 19.19 | 28.5579 |  | 20 | 20 | -- | 1.125 | 227 | 337.8132
5 | 5.563 | X-Stg. | 0.375 | 20.78 | 30.924 |  | 20 | 20 | -- | 1.25 | 250 | 372.041
5 | 5.563 | 120 | 0.5 | 27.1 | 40.3292 |  | 20 | 20 | 100 | 1.281 | 256 | 380.97
5 | 5.563 | 160 | 0.625 | 32.96 | 49.0499 |  | 20 | 20 | -- | 1.375 | 274 | 407.7569
5 | 5.563 | XX-Stg. | 0.75 | 38.55 | 57.3687 |  | 20 | 20 | 120 | 1.5 | 297 | 441.9847
[7 empty] | 20 | 20 | 140 | 1.75 | 342 | 508.9521
6 | 6.625 | 12 Ga. | 0.104 | 7.25 | 10.7892 |  | 20 | 20 | 160 | 1.969 | 379 | 564.0142
6 | 6.625 | 10S | 0.134 | 9.29 | 13.825
6 | 6.625 | 8 Ga. | 0.164 | 11.33 | 16.8609 |  | 22 | 22 | 8 Ga. | 0.164 | 38 | 56.5502
6 | 6.625 | API | 0.188 | 12.93 | 19.242 |  | 22 | 22 | 6 Ga. | 0.194 | 45 | 66.9674
6 | 6.625 | 6Ga. | 0.194 | 13.34 | 19.8521 |  | 22 | 22 | 3 Ga. | 0.239 | 56 | 83.3372
6 | 6.625 | API | 0.219 | 15.02 | 22.3522 |  | 22 | 22 | API | 0.25 | 58 | 86.3135
6 | 6.625 | API | 0.25 | 17.02 | 25.3286 |  | 22 | 22 | API | 0.281 | 65 | 96.7307
6 | 6.625 | API | 0.277 | 18.86 | 28.0668 |  | 22 | 22 | API | 0.312 | 72 | 107.1478
6 | 6.625 | Std. | 0.28 | 18.97 | 28.2305 |  | 22 | 22 | API | 0.344 | 80 | 119.0531
6 | 6.625 | API | 0.312 | 21.05 | 31.3259 |  | 22 | 22 | API | 0.375 | 87 | 129.4703
6 | 6.625 | API | 0.344 | 23.09 | 34.3617 |  | 22 | 22 | API | 0.406 | 94 | 139.8874
6 | 6.625 | API | 0.375 | 25.1 | 37.3529 |  | 22 | 22 | API | 0.438 | 101 | 150.3046
6 | 6.625 | X-Stg. | 0.432 | 28.57 | 42.5168 |  | 22 | 22 | API | 0.5 | 115 | 171.1389
6 | 6.625 | -- | 0.5 | 32.79 | 48.7969 |  | 22 | 22 | -- | 0.625 | 143 | 212.8075
6 | 6.625 | 120 | 0.562 | 36.4 | 54.1692 |  | 22 | 22 | -- | 0.75 | 170 | 252.9879
6 | 6.625 | 160 | 0.719 | 45.3 | 67.4138 |  | 22 | 22 | -- | 0.875 | 198 | 294.6565
6 | 6.625 | XX-Stg. | 0.864 | 53.16 | 79.1108 |  | 22 | 22 | -- | 1 | 224 | 333.3487
[7 empty] | 22 | 22 | -- | 1.125 | 251 | 373.5292
8 | 8.625 | 12 Ga. | 0.104 | 9.47 | 14.0929 |  | 22 | 22 | -- | 1.25 | 277 | 412.2214
8 | 8.625 | 10 Ga. | 0.134 | 12.16 | 18.0961 |  | 22 | 22 | -- | 1.375 | 303 | 450.9137
8 | 8.625 | 10S | 0.148 | 13.4 | 19.9414 |  | 22 | 22 | -- | 1.5 | 329 | 489.606
8 | 8.625 | 8 Ga. | 0.164 | 14.83 | 22.0695
8 | 8.625 | API | 0.188 | 16.9 | 25.15 |  | 24 | 24 | 8 Ga. | 0.164 | 42 | 62.5029
8 | 8.625 | 6 Ga. | 0.194 | 17.48 | 26.0131 |  | 24 | 24 | 6 Ga. | 0.194 | 49 | 72.92
8 | 8.625 | API | 0.203 | 18.3 | 27.2334 |  | 24 | 24 | 3 Ga. | 0.239 | 61 | 90.778
8 | 8.625 | API | 0.219 | 19.64 | 29.2275 |  | 24 | 24 | 10 | 0.25 | 63 | 93.7543
8 | 8.625 | 3 Ga. | 0.239 | 21.42 | 31.8765 |  | 24 | 24 | API | 0.281 | 71 | 105.6596
8 | 8.625 | 20 | 0.25 | 22.4 | 33.3349 |  | 24 | 24 | API | 0.312 | 79 | 117.565
8 | 8.625 | 30 | 0.277 | 24.7 | 36.7577 |  | 24 | 24 | API | 0.344 | 87 | 129.4703
8 | 8.625 | API | 0.312 | 27.72 | 41.2519 |  | 24 | 24 | Std. | 0.375 | 95 | 141.3756
8 | 8.625 | Std. | 0.322 | 28.55 | 42.4871 |  | 24 | 24 | API | 0.406 | 102 | 151.7927
8 | 8.625 | API | 0.344 | 30.4 | 45.2402 |  | 24 | 24 | API | 0.438 | 110 | 163.698
8 | 8.625 | API | 0.375 | 33.1 | 49.2582 |  | 24 | 24 | X-Stg. | 0.5 | 125 | 186.0205
8 | 8.625 | 60 | 0.406 | 35.7 | 53.1275 |  | 24 | 24 | 30 | 0.562 | 141 | 209.8311
8 | 8.625 | API | 0.438 | 38.33 | 57.0413 |  | 24 | 24 | -- | 0.625 | 156 | 232.1536
8 | 8.625 | X-Stg. | 0.5 | 43.39 | 64.5714 |  | 24 | 24 | 40 | 0.688 | 171 | 254.4761
8 | 8.625 | 100 | 0.594 | 50.9 | 75.7475 |  | 24 | 24 | -- | 0.75 | 186 | 276.7985
8 | 8.625 | -- | 0.625 | 53.4 | 79.468 |  | 24 | 24 | -- | 0.875 | 216 | 321.4434
8 | 8.625 | 120 | 0.719 | 60.7 | 90.3316 |  | 24 | 24 | 60 | 0.969 | 238 | 354.183
8 | 8.625 | 140 | 0.812 | 67.8 | 100.8975 |  | 24 | 24 | -- | 1 | 246 | 366.0884
8 | 8.625 | XX-Stg. | 0.875 | 72.42 | 107.7728 |  | 24 | 24 | -- | 1.125 | 275 | 409.2451
8 | 8.625 | 160 | 0.906 | 74.7 | 111.1659 |  | 24 | 24 | 80 | 1.219 | 297 | 441.9847
[7 empty] | 24 | 24 | -- | 1.25 | 304 | 452.4019
10 | 10.75 | 12 Ga. | 0.104 | 11.83 | 17.605 |  | 24 | 24 | -- | 1.375 | 332 | 494.0705
10 | 10.75 | 10 Ga. | 0.134 | 15.21 | 22.635 |  | 24 | 24 | -- | 1.5 | 361 | 537.2272
10 | 10.75 | 8 Ga. | 0.164 | 18.56 | 27.6203 |  | 24 | 24 | 100 | 1.531 | 367 | 546.1562
10 | 10.75 | 10S | 0.165 | 18.65 | 27.7543 |  | 24 | 24 | 120 | 1.812 | 429 | 638.4224
10 | 10.75 | API | 0.188 | 21.12 | 31.43 |  | 24 | 24 | 140 | 2.062 | 484 | 720.2714
10 | 10.75 | 6 Ga. | 0.194 | 21.89 | 32.5759 |  | 24 | 24 | 160 | 2.344 | 542 | 806.5849
10 | 10.75 | API | 0.203 | 22.86 | 34.0194
10 | 10.75 | API | 0.219 | 24.6 | 36.6088 |  | 26 | 26 | 8 Ga. | 0.164 | 45 | 66.9674
10 | 10.75 | 3 Ga. | 0.239 | 28.05 | 41.743 |  | 26 | 26 | 6 Ga. | 0.194 | 54 | 80.3609
10 | 10.75 | 20 | 0.25 | 28.03 | 41.7132 |  | 26 | 26 | 3 Ga. | 0.239 | 66 | 98.2188
10 | 10.75 | API | 0.279 | 31.2 | 46.4307 |  | 26 | 26 | API | 0.25 | 67 | 99.707
10 | 10.75 | 30 | 0.307 | 34.24 | 50.9547 |  | 26 | 26 | API | 0.281 | 77 | 114.5886
10 | 10.75 | API | 0.344 | 38.26 | 56.9372 |  | 26 | 26 | API | 0.312 | 84 | 125.0058
10 | 10.75 | Std. | 0.365 | 40.48 | 60.2409 |  | 26 | 26 | API | 0.344 | 94 | 139.8874
10 | 10.75 | API | 0.438 | 48.28 | 71.8486 |  | 26 | 26 | API | 0.375 | 103 | 153.2809
10 | 10.75 | X-Stg. | 0.5 | 54.74 | 81.4621 |  | 26 | 26 | API | 0.406 | 111 | 165.1862
10 | 10.75 | 80 | 0.594 | 64.4 | 95.8378 |  | 26 | 26 | API | 0.438 | 120 | 178.5797
10 | 10.75 | 100 | 0.719 | 77 | 114.5886 |  | 26 | 26 | API | 0.5 | 136 | 202.3903
10 | 10.75 | -- | 0.75 | 80.1 | 119.2019 |  | 26 | 26 | -- | 0.625 | 169 | 251.4997
10 | 10.75 | 120 | 0.844 | 89.2 | 132.7442 |  | 26 | 26 | -- | 0.75 | 202 | 300.6091
10 | 10.75 | 140 | 1 | 104.2 | 155.0667 |  | 26 | 26 | -- | 0.875 | 235 | 349.7186
10 | 10.75 | 160 | 1.125 | 116 | 172.627 |  | 26 | 26 | -- | 1 | 267 | 397.3398
[7 empty] | 26 | 26 | -- | 1.125 | 299 | 444.961
12 | 12.75 | 12 Ga. | 0.104 | 14.1 | 20.9831 |  | 26 | 26 | -- | 1.375 | 362 | 538.7154
12 | 12.75 | 10 Ga. | 0.134 | 18.1 | 26.9358 |  | 26 | 26 | -- | 1.5 | 393 | 584.8485
12 | 12.75 | 8 Ga. | 0.164 | 22.1 | 32.8884
12 | 12.75 | 10S | 0.18 | 24.2 | 36.0136 |  | 30 | 30 | 8 Ga. | 0.164 | 52 | 77.3845
12 | 12.75 | 6 Ga. | 0.194 | 26 | 38.6923 |  | 30 | 30 | 6 Ga. | 0.194 | 62 | 92.2662
12 | 12.75 | API | 0.203 | 27.2 | 40.4781 |  | 30 | 30 | 3 Ga. | 0.239 | 76 | 113.1005
12 | 12.75 | API | 0.219 | 29.3 | 43.6032 |  | 30 | 30 | API | 0.25 | 79 | 117.565
12 | 12.75 | 3 Ga. | 0.239 | 32 | 47.6212 |  | 30 | 30 | API | 0.281 | 89 | 132.4466
12 | 12.75 | 20 | 0.25 | 33.4 | 49.7047 |  | 30 | 30 | 10 | 0.312 | 99 | 147.3282
12 | 12.75 | API | 0.281 | 37.4 | 55.6573 |  | 30 | 30 | API | 0.344 | 109 | 162.2099
12 | 12.75 | API | 0.312 | 41.5 | 61.7588 |  | 30 | 30 | API | 0.375 | 119 | 177.0915
12 | 12.75 | 30 | 0.33 | 43.8 | 65.1816 |  | 30 | 30 | API | 0.406 | 130 | 193.4613
12 | 12.75 | API | 0.344 | 45.5 | 67.7115 |  | 30 | 30 | API | 0.438 | 138 | 205.3666
12 | 12.75 | Std. | 0.375 | 49.6 | 73.8129 |  | 30 | 30 | 20 | 0.5 | 158 | 235.1299
12 | 12.75 | 40 | 0.406 | 53.6 | 79.7656 |  | 30 | 30 | 30 | 0.625 | 196 | 291.6802
12 | 12.75 | API | 0.438 | 57.5 | 85.5694 |  | 30 | 30 | -- | 0.75 | 234 | 348.2304
12 | 12.75 | X-Stg. | 0.5 | 65.4 | 97.3259 |  | 30 | 30 | -- | 0.875 | 272 | 404.7806
12 | 12.75 | 60 | 0.562 | 73.2 | 108.9336 |  | 30 | 30 | -- | 1 | 310 | 461.3309
12 | 12.75 | -- | 0.625 | 80.9 | 120.3925 |  | 30 | 30 | -- | 1.125 | 347 | 516.3929
12 | 12.75 | 80 | 0.688 | 88.6 | 131.8513 |  | 30 | 30 | -- | 1.25 | 384 | 571.455
12 | 12.75 | -- | 0.75 | 96.2 | 143.1614 |  | 30 | 30 | -- | 1.375 | 421 | 626.5171
12 | 12.75 | 100 | 0.844 | 108 | 160.7217 |  | 30 | 30 | -- | 1.5 | 457 | 680.091
12 | 12.75 | -- | 0.875 | 110.9 | 165.0374
12 | 12.75 | 120 | 1 | 125.5 | 186.7646 |  | 32 | 32 | API | 0.25 | 85 | 126.4939
12 | 12.75 | 140 | 1.125 | 140 | 208.343 |  | 32 | 32 | API | 0.281 | 95 | 141.3756
12 | 12.75 | -- | 1.25 | 153.6 | 228.582 |  | 32 | 32 | API | 0.312 | 106 | 157.7454
12 | 12.75 | 160 | 1.312 | 161 | 239.5944 |  | 32 | 32 | API | 0.344 | 116 | 172.627
12 | 12.75 | -- | 1.375 | 167.2 | 248.821 |  | 32 | 32 | API | 0.375 | 127 | 188.9968
12 | 12.75 | -- | 1.5 | 180.4 | 268.4648 |  | 32 | 32 | API | 0.406 | 137 | 203.8785
[7 empty] | 32 | 32 | API | 0.438 | 148 | 220.2483
[7 empty] | 32 | 32 | API | 0.5 | 168 | 250.0116
[7 empty] | 32 | 32 | -- | 0.625 | 209 | 311.0263
[7 empty] | 32 | 32 | -- | 0.75 | 250 | 372.041
[7 empty] | 32 | 32 | -- | 0.875 | 291 | 433.0557
[7 empty] | 32 | 32 | -- | 1 | 331 | 492.5823
[7 empty] | 32 | 32 | -- | 1.125 | 371 | 552.1089
[7 empty] | 32 | 32 | -- | 1.25 | 410 | 610.1473
[7 empty] | 32 | 32 | -- | 1.375 | 450 | 669.6738
[7 empty] | 32 | 32 | -- | 1.5 | 489 | 727.7122
[7 empty] | 34 | 34 | API | 0.25 | 90 | 133.9348
[7 empty] | 34 | 34 | API | 0.281 | 101 | 150.3046
[7 empty] | 34 | 34 | API | 0.312 | 112 | 166.6744
[7 empty] | 34 | 34 | API | 0.344 | 124 | 184.5323
[7 empty] | 34 | 34 | API | 0.375 | 135 | 200.9021
[7 empty] | 34 | 34 | API | 0.406 | 146 | 217.272
[7 empty] | 34 | 34 | API | 0.438 | 157 | 233.6418
[7 empty] | 34 | 34 | API | 0.5 | 179 | 266.3814
[7 empty] | 34 | 34 | -- | 0.625 | 223 | 331.8606
[7 empty] | 34 | 34 | -- | 0.75 | 266 | 395.8516
[7 empty] | 34 | 34 | -- | 0.875 | 308 | 458.3545
[7 empty] | 34 | 34 | -- | 1 | 353 | 525.3219
[7 empty] | 34 | 34 | -- | 1.125 | 395 | 587.8248
[7 empty] | 34 | 34 | -- | 1.25 | 437 | 650.3277
[7 empty] | 34 | 34 | -- | 1.375 | 479 | 712.8306
[7 empty] | 34 | 34 | -- | 1.5 | 521 | 775.3335
[7 empty] | 36 | 36 | -- | 0.164 | 63 | 93.7543
[7 empty] | 36 | 36 | -- | 0.194 | 74 | 110.1241
[7 empty] | 36 | 36 | -- | 0.239 | 91 | 135.4229
[7 empty] | 36 | 36 | API | 0.25 | 96 | 142.8637
[7 empty] | 36 | 36 | API | 0.281 | 107 | 159.2336
[7 empty] | 36 | 36 | API | 0.312 | 119 | 177.0915
[7 empty] | 36 | 36 | API | 0.344 | 131 | 194.9495
[7 empty] | 36 | 36 | API | 0.375 | 143 | 212.8075
[7 empty] | 36 | 36 | API | 0.406 | 154 | 229.1773
[7 empty] | 36 | 36 | API | 0.438 | 166 | 247.0352
[7 empty] | 36 | 36 | API | 0.5 | 190 | 282.7512
[7 empty] | 36 | 36 | -- | 0.625 | 236 | 351.2067
[7 empty] | 36 | 36 | -- | 0.75 | 282 | 419.6623
[7 empty] | 36 | 36 | -- | 0.875 | 329 | 489.606
[7 empty] | 36 | 36 | -- | 1 | 374 | 556.5734
[7 empty] | 36 | 36 | -- | 1.125 | 419 | 623.5407
[7 empty] | 36 | 36 | -- | 1.25 | 464 | 690.5081
[7 empty] | 36 | 36 | -- | 1.375 | 509 | 757.4755
[7 empty] | 36 | 36 | -- | 1.5 | 553 | 822.9547
[7 empty] | 42 | 42 | -- | 0.25 | 112 | 166.6744
[7 empty] | 42 | 42 | -- | 0.375 | 167 | 248.5234
[7 empty] | 42 | 42 | -- | 0.5 | 222 | 330.3724
[7 empty] | 42 | 42 | -- | 0.625 | 276 | 410.7333
[7 empty] | 42 | 42 | -- | 0.75 | 331 | 492.5823
[7 empty] | 42 | 42 | -- | 0.875 | 385 | 572.9432
[7 empty] | 42 | 42 | -- | 1 | 438 | 651.8159
[7 empty] | 42 | 42 | -- | 1.125 | 492 | 732.1767
[7 empty] | 42 | 42 | -- | 1.25 | 544 | 809.5612
[7 empty] | 42 | 42 | -- | 1.375 | 597 | 888.4339
[7 empty] | 42 | 42 | -- | 1.5 | 649 | 965.8185
Z
I
R
Note on B5: Enter Pipe Diameter in Inches
Note on C5: Enter Pipe Wall Thickness in Inches

## ELL. Head Dim
|  |  |  | Inches | 115.2 | Approximate area for nozzle attachment
| Start of Knuckle Radius |  |  | mm | 2926.08
Inside Depth
|  | Knuckle Radius | [9 empty] | I.D./4
| Inches | 24.8688 | [9 empty] | 36 | Inches
| mm | 631.6675 | [9 empty] | 914.4 | mm
[5 empty] | 47.1312 | Inches |  | Dish Radius
| Note | [6 empty] | 130.248 | Inches
| Verify all dimension |  |  |  | 1197.1325 | mm |  | 3308.2992 | mm
with vendor drawings
[6 empty] | 144 | Inches
[6 empty] | 3657.6 | mm
All Dimensions
are in Inches (mm)
Verify all dimension
with vendor drawings
Not all wall thicknesses are shown. Interpolate
for approximate inside depth O.D. dish IDD
| Inches (Flanged & Dished Head Table) | [5 empty] | Millimeters (Flanged & Dished Head Table)
| O.D | "T" | "R1" | "R2" | IDD |  | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.38 | 24 | 1.13 | 4.25 |  |  | 9.652 | 609.6 | 28.702 | 107.95
|  | 0.5 | 24 | 1.5 | 4.38 |  | 26" | 12.7 | 609.6 | 38.1 | 111.252
|  | 0.63 | 24 | 1.88 | 4.5 |  | 660 | 16.002 | 609.6 | 47.752 | 114.3
|  | 0.75 | 24 | 2.25 | 4.69 |  |  | 19.05 | 609.6 | 57.15 | 119.126
|  | 0.38 | 26 | 4.5 | 4.5 |  |  | 9.652 | 660.4 | 114.3 | 114.3
|  | 0.5 | 26 | 4.63 | 4.63 |  | 28" | 12.7 | 660.4 | 117.602 | 117.602
|  | 0.63 | 26 | 4.75 | 4.75 |  | 711 | 16.002 | 660.4 | 120.65 | 120.65
|  | 0.75 | 26 | 4.94 | 4.94 |  |  | 19.05 | 660.4 | 125.476 | 125.476
|  | 0.38 | 30 | 4.5 | 4.5 |  |  | 9.652 | 762 | 114.3 | 114.3
|  | 0.5 | 30 | 4.63 | 4.63 |  | 30" | 12.7 | 762 | 117.602 | 117.602
|  | 0.63 | 30 | 4.81 | 4.81 |  | 762 | 16.002 | 762 | 122.174 | 122.174
|  | 0.75 | 30 | 5 | 5 |  |  | 19.05 | 762 | 127 | 127
|  | 0.38 | 30 | 5 | 5 |  |  | 9.652 | 762 | 127 | 127
|  | 0.5 | 30 | 5.19 | 5.19 |  | 32" | 12.7 | 762 | 131.826 | 131.826
|  | 0.63 | 30 | 5.31 | 5.31 |  | 812.8 | 16.002 | 762 | 134.874 | 134.874
|  | 0.75 | 30 | 5.5 | 5.5 |  |  | 19.05 | 762 | 139.7 | 139.7
|  | 0.38 | 34 | 5 | 5 |  |  | 9.652 | 863.6 | 127 | 127
|  | 0.5 | 34 | 5.19 | 5.19 |  | 34 | 12.7 | 863.6 | 131.826 | 131.826
|  | 0.63 | 33 | 5.44 | 5.44 |  | 864 | 16.002 | 838.2 | 138.176 | 138.176
|  | 0.75 | 30 | 6.06 | 6.06 |  |  | 19.05 | 762 | 153.924 | 153.924
|  | 0.38 | 36 | 5.25 | 5.25 |  |  | 9.652 | 914.4 | 133.35 | 133.35
|  | 0.5 | 36 | 5.44 | 5.44 |  | 36" | 12.7 | 914.4 | 138.176 | 138.176
|  | 0.63 | 36 | 5.63 | 5.63 |  | 914.4 | 16.002 | 914.4 | 143.002 | 143.002
|  | 0.75 | 36 | 5.75 | 5.75 |  |  | 19.05 | 914.4 | 146.05 | 146.05
| O.D | "T" | "R1" | "R2" | IDD |  | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.38 | 36 | 1.13 | 5.81 |  |  | 9.652 | 914.4 | 28.702 | 147.574
|  | 0.5 | 36 | 1.5 | 6 |  | 38" | 12.7 | 914.4 | 38.1 | 152.4
|  | 0.63 | 36 | 1.88 | 6.13 |  | 965.2 | 16.002 | 914.4 | 47.752 | 155.702
|  | 0.75 | 36 | 2.25 | 6.31 |  |  | 19.05 | 914.4 | 57.15 | 160.274
|  | 0.38 | 40 | 1.13 | 5.81 |  |  | 9.652 | 1016 | 28.702 | 147.574
|  | 0.5 | 40 | 1.5 | 5.94 |  | 40" | 12.7 | 1016 | 38.1 | 150.876
|  | 0.63 | 36 | 1.88 | 6.69 |  | 1016 | 16.002 | 914.4 | 47.752 | 169.926
|  | 0.75 | 36 | 2.25 | 6.88 |  |  | 19.05 | 914.4 | 57.15 | 174.752
|  | 0.38 | 42 | 1.13 | 6.06 |  |  | 9.652 | 1066.8 | 28.702 | 153.924
|  | 0.5 | 42 | 1.5 | 6.25 |  | 42" | 12.7 | 1066.8 | 38.1 | 158.75
|  | 0.63 | 42 | 1.88 | 6.38 |  | 1066.8 | 16.002 | 1066.8 | 47.752 | 162.052
|  | 0.75 | 40 | 2.25 | 6.81 |  |  | 19.05 | 1016 | 57.15 | 172.974
|  | 0.38 | 48 | 1.13 | 6.88 |  |  | 9.652 | 1219.2 | 28.702 | 174.752
|  | 0.5 | 48 | 1.5 | 7 |  | 42" | 12.7 | 1219.2 | 38.1 | 177.8
|  | 0.63 | 48 | 1.88 | 7.19 |  | 1219.2 | 16.002 | 1219.2 | 47.752 | 182.626
|  | 0.75 | 48 | 2.25 | 7.38 |  |  | 19.05 | 1219.2 | 57.15 | 187.452
|  | 0.38 | 54 | 1.13 | 7.69 |  |  | 9.652 | 1371.6 | 28.702 | 195.326
|  | 0.5 | 54 | 1.5 | 7.81 |  | 54" | 12.7 | 1371.6 | 38.1 | 198.374
|  | 0.63 | 54 | 1.88 | 8 |  | 1371.6 | 16.002 | 1371.6 | 47.752 | 203.2
|  | 0.75 | 54 | 2.25 | 8.19 |  |  | 19.05 | 1371.6 | 57.15 | 208.026
|  | 0.38 | 60 | 1.13 | 8.5 |  |  | 9.652 | 1524 | 28.702 | 215.9
|  | 0.5 | 60 | 1.5 | 8.63 |  | 60" | 12.7 | 1524 | 38.1 | 219.202
|  | 0.63 | 60 | 1.88 | 8.81 |  | 1524 | 16.002 | 1524 | 47.752 | 223.774
|  | 0.75 | 60 | 2.25 | 8.94 |  |  | 19.05 | 1524 | 57.15 | 227.076
| O.D | "T" | "R1" | "R2" | IDD |  | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.38 | 66 | 1.13 | 9.31 |  |  | 9.652 | 1676.4 | 28.702 | 236.474
|  | 0.5 | 66 | 1.5 | 9.44 |  | 66" | 12.7 | 1676.4 | 38.1 | 239.776
|  | 0.63 | 66 | 1.88 | 9.63 |  | 1676.4 | 16.002 | 1676.4 | 47.752 | 244.602
|  | 0.75 | 66 | 2.25 | 9.75 |  |  | 19.05 | 1676.4 | 57.15 | 247.65
|  | 0.38 | 72 | 1.13 | 10.06 |  |  | 9.652 | 1828.8 | 28.702 | 255.524
|  | 0.63 | 72 | 1.88 | 10.38 |  | 72" | 16.002 | 1828.8 | 47.752 | 263.652
|  | 0.88 | 72 | 2.63 | 10.69 |  | 1828.8 | 22.352 | 1828.8 | 66.802 | 271.526
|  | 1.13 | 72 | 3.38 | 11 |  |  | 28.702 | 1828.8 | 85.852 | 279.4
|  | 0.38 | 78 | 1.13 | 10.88 |  |  | 9.652 | 1981.2 | 28.702 | 276.352
|  | 0.63 | 78 | 1.88 | 11.19 |  | 78" | 16.002 | 1981.2 | 47.752 | 284.226
|  | 0.88 | 78 | 2.63 | 11.5 |  | 1981.2 | 22.352 | 1981.2 | 66.802 | 292.1
|  | 1.13 | 78 | 3.38 | 11.81 |  |  | 28.702 | 1981.2 | 85.852 | 299.974
|  | 0.38 | 84 | 1.13 | 11.69 |  |  | 9.652 | 2133.6 | 28.702 | 296.926
|  | 0.63 | 84 | 1.88 | 11.88 |  | 84" | 16.002 | 2133.6 | 47.752 | 301.752
|  | 0.88 | 84 | 2.63 | 12.31 |  | 2133.6 | 22.352 | 2133.6 | 66.802 | 312.674
|  | 1.13 | 84 | 3.38 | 12.63 |  |  | 28.702 | 2133.6 | 85.852 | 320.802
|  | 0.38 | 90 | 1.13 | 12.5 |  |  | 9.652 | 2286 | 28.702 | 317.5
|  | 0.63 | 84 | 1.88 | 13.75 |  | 90" | 16.002 | 2133.6 | 47.752 | 349.25
|  | 0.88 | 84 | 2.63 | 14 |  | 2286 | 22.352 | 2133.6 | 66.802 | 355.6
|  | 1.13 | 84 | 3.38 | 14.31 |  |  | 28.702 | 2133.6 | 85.852 | 363.474
|  | 0.5 | 96 | 1.5 | 13.44 |  |  | 12.7 | 2438.4 | 38.1 | 341.376
|  | 0.75 | 96 | 2.25 | 13.75 |  | 96" | 19.05 | 2438.4 | 57.15 | 349.25
|  | 1 | 96 | 3 | 14.06 |  | 2438.4 | 25.4 | 2438.4 | 76.2 | 357.124
|  | 1.25 | 96 | 3.75 | 14.38 |  |  | 31.75 | 2438.4 | 95.25 | 365.252
| O.D | "T" | "R1" | "R2" | IDD |  | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.5 | 102 | 1.5 | 14.25 |  |  | 12.7 | 2590.8 | 38.1 | 361.95
|  | 0.75 | 96 | 2.25 | 15.5 |  | 102" | 19.05 | 2438.4 | 57.15 | 393.7
|  | 1 | 96 | 3 | 15.75 |  | 2590.8 | 25.4 | 2438.4 | 76.2 | 400.05
|  | 1.25 | 96 | 3.75 | 16.06 |  |  | 31.75 | 2438.4 | 95.25 | 407.924
|  | 0.5 | 108 | 1.5 | 15.06 |  |  | 12.7 | 2743.2 | 38.1 | 382.524
|  | 0.75 | 108 | 2.25 | 15.38 |  | 108" | 19.05 | 2743.2 | 57.15 | 390.652
|  | 1 | 102 | 3 | 16.56 |  | 2743.2 | 25.4 | 2590.8 | 76.2 | 420.624
|  | 1.25 | 102 | 3.75 | 16.81 |  |  | 31.75 | 2590.8 | 95.25 | 426.974
|  | 0.5 | 114 | 1.5 | 15.88 |  |  | 12.7 | 2895.6 | 38.1 | 403.352
|  | 0.75 | 114 | 2.25 | 16.19 |  | 114" | 19.05 | 2895.6 | 57.15 | 411.226
|  | 1 | 108 | 3 | 17.38 |  | 2895.6 | 25.4 | 2743.2 | 76.2 | 441.452
|  | 1.25 | 108 | 3.75 | 17.63 |  |  | 31.75 | 2743.2 | 95.25 | 447.802
|  | 0.5 | 120 | 1.5 | 16.69 |  |  | 12.7 | 3048 | 38.1 | 423.926
|  | 0.88 | 120 | 2.63 | 17.13 |  | 120" | 22.352 | 3048 | 66.802 | 435.102
|  | 1.25 | 120 | 3.75 | 17.59 |  | 3048 | 31.75 | 3048 | 95.25 | 446.786
|  | 1.63 | 120 | 4.88 | 18.06 |  |  | 41.402 | 3048 | 123.952 | 458.724
|  | 0.5 | 126 | 1.5 | 17.5 |  |  | 12.7 | 3200.4 | 38.1 | 444.5
|  | 0.88 | 120 | 2.63 | 18.81 |  | 126" | 22.352 | 3048 | 66.802 | 477.774
|  | 1.25 | 120 | 3.75 | 19.25 |  | 3200.4 | 31.75 | 3048 | 95.25 | 488.95
|  | 1.63 | 120 | 4.88 | 19.69 |  |  | 41.402 | 3048 | 123.952 | 500.126
|  | 0.63 | 132 | 1.88 | 18.44 |  |  | 16.002 | 3352.8 | 47.752 | 468.376
|  | 0.88 | 132 | 2.63 | 18.75 |  | 132" | 22.352 | 3352.8 | 66.802 | 476.25
|  | 1.13 | 132 | 3.38 | 19 |  | 3352.8 | 28.702 | 3352.8 | 85.852 | 482.6
|  | 1.5 | 132 | 4.5 | 19.5 |  |  | 38.1 | 3352.8 | 114.3 | 495.3
| O.D | "T" | "R1" | "R2" | IDD |  | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.63 | 132 | 1.88 | 20.13 |  |  | 16.002 | 3352.8 | 47.752 | 511.302
|  | 0.88 | 132 | 2.63 | 20.44 |  | 138" | 22.352 | 3352.8 | 66.802 | 519.176
|  | 1.13 | 132 | 3.38 | 20.69 |  | 3505.2 | 28.702 | 3352.8 | 85.852 | 525.526
|  | 1.5 | 132 | 4.5 | 21.13 |  |  | 38.1 | 3352.8 | 114.3 | 536.702
|  | 0.63 | 144 | 1.88 | 20 |  |  | 16.002 | 3657.6 | 47.752 | 508
|  | 0.88 | 144 | 2.63 | 20.31 |  | 144" | 22.352 | 3657.6 | 66.802 | 515.874
|  | 1.13 | 144 | 3.38 | 20.63 |  | 3657.6 | 28.702 | 3657.6 | 85.852 | 524.002
|  | 1.5 | 144 | 4.5 | 21.13 |  |  | 38.1 | 3657.6 | 114.3 | 536.702
|  | 0.75 | 144 | 2.25 | 23.69 |  |  | 19.05 | 3657.6 | 57.15 | 601.726
|  | 1.13 | 144 | 3.38 | 24.13 |  | 156" | 28.702 | 3657.6 | 85.852 | 612.902
|  | 1.5 | 144 | 4.5 | 24.5 |  | 3962.4 | 38.1 | 3657.6 | 114.3 | 622.3
|  | 1.88 | 144 | 5.63 | 24.94 |  |  | 47.752 | 3657.6 | 143.002 | 633.476
|  | 0.75 | 170 | 2.25 | 23.13 |  |  | 19.05 | 4318 | 57.15 | 587.502
|  | 1.13 | 170 | 3.38 | 23.56 |  | 168" | 28.702 | 4318 | 85.852 | 598.424
|  | 1.5 | 170 | 4.5 | 24.06 |  | 4267.2 | 38.1 | 4318 | 114.3 | 611.124
|  | 1.88 | 170 | 5.63 | 24.19 |  |  | 47.752 | 4318 | 143.002 | 614.426
|  | 0.88 | 170 | 2.63 | 26.69 |  |  | 22.352 | 4318 | 66.802 | 677.926
|  | 1.25 | 170 | 3.75 | 27.13 |  | 180 | 31.75 | 4318 | 95.25 | 689.102
|  | 1.63 | 170 | 4.88 | 27.56 |  | 4572 | 41.402 | 4318 | 123.952 | 700.024
|  | 2 | 170 | 6 | 28 |  |  | 50.8 | 4318 | 152.4 | 711.2
|  | 0.88 | 170 | 2.63 | 30.5 |  |  | 22.352 | 4318 | 66.802 | 774.7
|  | 1.25 | 170 | 3.75 | 30.88 |  | 192" | 31.75 | 4318 | 95.25 | 784.352
|  | 1.63 | 170 | 4.88 | 31.25 |  | 4876.8 | 41.402 | 4318 | 123.952 | 793.75
|  | 2 | 170 | 6 | 31.63 |  |  | 50.8 | 4318 | 152.4 | 803.402
| O.D | "T" | "R1" | "R2" | IDD |  | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.88 | 170 | 2.63 | 34.63 |  |  | 22.352 | 4318 | 66.802 | 879.602
|  | 1.25 | 170 | 3.75 | 35 |  | 204" | 31.75 | 4318 | 95.25 | 889
|  | 1.63 | 170 | 4.88 | 35.31 |  | 5181.6 | 41.402 | 4318 | 123.952 | 896.874
|  | 2 | 170 | 6 | 35.63 |  |  | 50.8 | 4318 | 152.4 | 905.002
|  | 0.88 | 170 | 2.63 | 39.06 |  |  | 22.352 | 4318 | 66.802 | 992.124
|  | 1.25 | 170 | 3.75 | 39.5 |  | 216" | 31.75 | 4318 | 95.25 | 1003.3
|  | 1.63 | 170 | 4.88 | 39.75 |  | 5486.4 | 41.402 | 4318 | 123.952 | 1009.65
|  | 2 | 170 | 6 | 40 |  |  | 50.8 | 4318 | 152.4 | 1016
|  | 0.88 | 180 | 2.63 | 41.25 |  |  | 22.352 | 4572 | 66.802 | 1047.75
|  | 1.25 | 180 | 3.75 | 41.5 |  | 228" | 31.75 | 4572 | 95.25 | 1054.1
|  | 1.63 | 180 | 4.88 | 41.75 |  | 5791.2 | 41.402 | 4572 | 123.952 | 1060.45
|  | 2 | 180 | 6 | 42 |  |  | 50.8 | 4572 | 152.4 | 1066.8
|  | 0.88 | 180 | 2.63 | 46.25 |  |  | 22.352 | 4572 | 66.802 | 1174.75
|  | 1.25 | 180 | 3.75 | 46.44 |  | 240" | 31.75 | 4572 | 95.25 | 1179.576
|  | 1.63 | 180 | 4.88 | 46.63 |  | 6096 | 41.402 | 4572 | 123.952 | 1184.402
|  | 2 | 180 | 6 | 46.81 |  |  | 50.8 | 4572 | 152.4 | 1188.974
All Dimensions
are in Inches (mm)
Verify all dimension
with vendor drawings
Not all wall thicknesses are shown. Interpolate
for approximate inside depth O.D. dish IDD
| Inches (Flanged & Dished Head ASME Table) | [5 empty] | Millimeters (Flanged & Dished Head ASME Table)
| O.D | "T" | "R1" | "R2" | IDD | ASME | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.38 | 24 | 1.63 | 4.5 |  |  | 9.652 | 609.6 | 41.402 | 114.3
|  | 0.5 | 24 | 1.63 | 4.44 |  | 26" | 12.7 | 609.6 | 41.402 | 112.776
|  | 0.63 | 24 | 1.88 | 4.5 |  | 660 | 16.002 | 609.6 | 47.752 | 114.3
|  | 0.75 | 24 | 2.25 | 4.69 |  |  | 19.05 | 609.6 | 57.15 | 119.126
|  | 0.38 | 26 | 1.75 | 4.81 |  |  | 9.652 | 660.4 | 44.45 | 122.174
|  | 0.5 | 26 | 1.75 | 4.75 |  | 28" | 12.7 | 660.4 | 44.45 | 120.65
|  | 0.63 | 26 | 1.88 | 4.75 |  | 711 | 16.002 | 660.4 | 47.752 | 120.65
|  | 0.75 | 26 | 2.25 | 4.94 |  |  | 19.05 | 660.4 | 57.15 | 125.476
|  | 0.38 | 30 | 1.88 | 4.88 |  |  | 9.652 | 762 | 47.752 | 123.952
|  | 0.5 | 30 | 1.88 | 4.81 |  | 30" | 12.7 | 762 | 47.752 | 122.174
|  | 0.63 | 30 | 1.88 | 4.81 |  | 762 | 16.002 | 762 | 47.752 | 122.174
|  | 0.75 | 30 | 2.25 | 5 |  |  | 19.05 | 762 | 57.15 | 127
|  | 0.38 | 30 | 2 | 5.56 |  |  | 9.652 | 762 | 50.8 | 141.224
|  | 0.5 | 30 | 2 | 5.5 |  | 32" | 12.7 | 762 | 50.8 | 139.7
|  | 0.63 | 30 | 2 | 5.38 |  | 812.8 | 16.002 | 762 | 50.8 | 136.652
|  | 0.75 | 30 | 2.25 | 5.5 |  |  | 19.05 | 762 | 57.15 | 139.7
|  | 0.38 | 34 | 2.13 | 5.56 |  |  | 9.652 | 863.6 | 54.102 | 141.224
|  | 0.5 | 34 | 2.13 | 5.5 |  | 34 | 12.7 | 863.6 | 54.102 | 139.7
|  | 0.63 | 30 | 2.13 | 6 |  | 864 | 16.002 | 762 | 54.102 | 152.4
|  | 0.75 | 30 | 2.25 | 6.06 |  |  | 19.05 | 762 | 57.15 | 153.924
|  | 0.38 | 36 | 2.25 | 5.94 |  |  | 9.652 | 914.4 | 57.15 | 150.876
|  | 0.5 | 36 | 2.25 | 5.88 |  | 36" | 12.7 | 914.4 | 57.15 | 149.352
|  | 0.63 | 36 | 2.25 | 5.81 |  | 914.4 | 16.002 | 914.4 | 57.15 | 147.574
|  | 0.75 | 36 | 2.25 | 5.75 |  |  | 19.05 | 914.4 | 57.15 | 146.05
| O.D | "T" | "R1" | "R2" | IDD | ASME | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.38 | 36 | 2.38 | 6.5 |  |  | 9.652 | 914.4 | 60.452 | 165.1
|  | 0.5 | 36 | 2.38 | 6.44 |  | 38" | 12.7 | 914.4 | 60.452 | 163.576
|  | 0.63 | 36 | 2.38 | 6.38 |  | 965.2 | 16.002 | 914.4 | 60.452 | 162.052
|  | 0.75 | 36 | 2.38 | 6.38 |  |  | 19.05 | 914.4 | 60.452 | 162.052
|  | 0.38 | 40 | 2.5 | 6.63 |  |  | 9.652 | 1016 | 63.5 | 168.402
|  | 0.5 | 40 | 2.5 | 6.56 |  | 40" | 12.7 | 1016 | 63.5 | 166.624
|  | 0.63 | 36 | 2.5 | 6.94 |  | 1016 | 16.002 | 914.4 | 63.5 | 176.276
|  | 0.75 | 36 | 2.5 | 7 |  |  | 19.05 | 914.4 | 63.5 | 177.8
|  | 0.38 | 40 | 2.63 | 7.19 |  |  | 9.652 | 1016 | 66.802 | 182.626
|  | 0.5 | 40 | 2.63 | 7.13 |  | 42" | 12.7 | 1016 | 66.802 | 181.102
|  | 0.63 | 40 | 2.63 | 7.06 |  | 1066.8 | 16.002 | 1016 | 66.802 | 179.324
|  | 0.75 | 40 | 2.63 | 7 |  |  | 19.05 | 1016 | 66.802 | 177.8
|  | 0.38 | 42 | 3 | 8 |  |  | 9.652 | 1066.8 | 76.2 | 203.2
|  | 0.5 | 42 | 3 | 8.75 |  | 42" | 12.7 | 1066.8 | 76.2 | 222.25
|  | 0.63 | 42 | 3 | 8.69 |  | 1219.2 | 16.002 | 1066.8 | 76.2 | 220.726
|  | 0.75 | 42 | 3 | 8.63 |  |  | 19.05 | 1066.8 | 76.2 | 219.202
|  | 0.38 | 54 | 3.25 | 8.94 |  |  | 9.652 | 1371.6 | 82.55 | 227.076
|  | 0.5 | 48 | 3.25 | 9.75 |  | 54" | 12.7 | 1219.2 | 82.55 | 247.65
|  | 0.63 | 48 | 3.25 | 9.75 |  | 1371.6 | 16.002 | 1219.2 | 82.55 | 247.65
|  | 0.75 | 48 | 3.25 | 9.63 |  |  | 19.05 | 1219.2 | 82.55 | 244.602
|  | 0.38 | 60 | 3.63 | 10 |  |  | 9.652 | 1524 | 92.202 | 254
|  | 0.5 | 60 | 3.63 | 9.88 |  | 60" | 12.7 | 1524 | 92.202 | 250.952
|  | 0.63 | 54 | 3.63 | 10.69 |  | 1524 | 16.002 | 1371.6 | 92.202 | 271.526
|  | 0.75 | 54 | 3.63 | 10.63 |  |  | 19.05 | 1371.6 | 92.202 | 270.002
| O.D | "T" | "R1" | "R2" | IDD | ASME | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.38 | 66 | 4 | 11 |  |  | 9.652 | 1676.4 | 101.6 | 279.4
|  | 0.5 | 60 | 4 | 10.94 |  | 66" | 12.7 | 1524 | 101.6 | 277.876
|  | 0.63 | 60 | 4 | 11.75 |  | 1676.4 | 16.002 | 1524 | 101.6 | 298.45
|  | 0.75 | 60 | 4 | 11.63 |  |  | 19.05 | 1524 | 101.6 | 295.402
|  | 0.38 | 72 | 4.38 | 12 |  |  | 9.652 | 1828.8 | 111.252 | 304.8
|  | 0.63 | 72 | 4.38 | 11.88 |  | 72" | 16.002 | 1828.8 | 111.252 | 301.752
|  | 0.75 | 72 | 4.38 | 11.88 |  | 1828.8 | 19.05 | 1828.8 | 111.252 | 301.752
|  | 0.88 | 66 | 4.38 | 12.63 |  |  | 22.352 | 1676.4 | 111.252 | 320.802
|  | 0.38 | 78 | 4.75 | 13 |  |  | 9.652 | 1981.2 | 120.65 | 330.2
|  | 0.5 | 72 | 4.75 | 13.81 |  | 78" | 12.7 | 1828.8 | 120.65 | 350.774
|  | 0.75 | 72 | 4.75 | 13.69 |  | 1981.2 | 19.05 | 1828.8 | 120.65 | 347.726
|  | 1 | 72 | 4.75 | 13.5 |  |  | 25.4 | 1828.8 | 120.65 | 342.9
|  | 0.38 | 84 | 5.13 | 14 |  |  | 9.652 | 2133.6 | 130.302 | 355.6
|  | 0.63 | 84 | 5.13 | 13.88 |  | 84" | 16.002 | 2133.6 | 130.302 | 352.552
|  | 0.88 | 84 | 5.13 | 13.75 |  | 2133.6 | 22.352 | 2133.6 | 130.302 | 349.25
|  | 1 | 84 | 5.13 | 13.69 |  |  | 25.4 | 2133.6 | 130.302 | 347.726
|  | 0.38 | 90 | 5.5 | 15.13 |  |  | 9.652 | 2286 | 139.7 | 384.302
|  | 0.5 | 84 | 5.5 | 15.81 |  | 90" | 12.7 | 2133.6 | 139.7 | 401.574
|  | 0.75 | 84 | 5.5 | 15.69 |  | 2286 | 19.05 | 2133.6 | 139.7 | 398.526
|  | 1 | 84 | 5.5 | 15.56 |  |  | 25.4 | 2133.6 | 139.7 | 395.224
|  | 0.38 | 96 | 5.88 | 16.13 |  |  | 9.652 | 2438.4 | 149.352 | 409.702
|  | 0.5 | 90 | 5.88 | 16.88 |  | 96" | 12.7 | 2286 | 149.352 | 428.752
|  | 0.88 | 90 | 5.88 | 16.63 |  | 2438.4 | 22.352 | 2286 | 149.352 | 422.402
|  | 1.25 | 90 | 5.88 | 16.44 |  |  | 31.75 | 2286 | 149.352 | 417.576
| O.D | "T" | "R1" | "R2" | IDD | ASME | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.5 | 96 | 6.13 | 17.88 |  |  | 12.7 | 2438.4 | 155.702 | 454.152
|  | 0.75 | 96 | 6.13 | 17.69 |  | 102" | 19.05 | 2438.4 | 155.702 | 449.326
|  | 1 | 96 | 6.13 | 17.56 |  | 2590.8 | 25.4 | 2438.4 | 155.702 | 446.024
|  | 1.13 | 90 | 6.13 | 18.5 |  |  | 28.702 | 2286 | 155.702 | 469.9
|  | 0.5 | 102 | 6.5 | 18.88 |  |  | 12.7 | 2590.8 | 165.1 | 479.552
|  | 0.75 | 102 | 6.5 | 18.75 |  | 108" | 19.05 | 2590.8 | 165.1 | 476.25
|  | 1 | 102 | 6.5 | 18.56 |  | 2743.2 | 25.4 | 2590.8 | 165.1 | 471.424
|  | 1.13 | 96 | 6.5 | 19.44 |  |  | 28.702 | 2438.4 | 165.1 | 493.776
|  | 0.5 | 108 | 6.88 | 19.88 |  |  | 12.7 | 2743.2 | 174.752 | 504.952
|  | 0.75 | 108 | 6.88 | 19.75 |  | 114" | 19.05 | 2743.2 | 174.752 | 501.65
|  | 1 | 108 | 6.88 | 19.63 |  | 2895.6 | 25.4 | 2743.2 | 174.752 | 498.602
|  | 1.25 | 108 | 6.88 | 19.5 |  |  | 31.75 | 2743.2 | 174.752 | 495.3
|  | 0.5 | 114 | 7.25 | 20.88 |  |  | 12.7 | 2895.6 | 184.15 | 530.352
|  | 0.88 | 114 | 7.25 | 20.69 |  | 120" | 22.352 | 2895.6 | 184.15 | 525.526
|  | 1.25 | 108 | 7.25 | 21.44 |  | 3048 | 31.75 | 2743.2 | 184.15 | 544.576
|  | 1.63 | 108 | 7.25 | 21.25 |  |  | 41.402 | 2743.2 | 184.15 | 539.75
|  | 0.5 | 120 | 7.63 | 21.88 |  |  | 12.7 | 3048 | 193.802 | 555.752
|  | 0.88 | 120 | 7.63 | 21.69 |  | 126" | 22.352 | 3048 | 193.802 | 550.926
|  | 1.25 | 120 | 7.63 | 21.5 |  | 3200.4 | 31.75 | 3048 | 193.802 | 546.1
|  | 1.38 | 114 | 7.63 | 22.31 |  |  | 35.052 | 2895.6 | 193.802 | 566.674
|  | 0.75 | 126 | 8 | 22.81 |  |  | 19.05 | 3200.4 | 203.2 | 579.374
|  | 0.88 | 120 | 8 | 23.69 |  | 132" | 22.352 | 3048 | 203.2 | 601.726
|  | 1.25 | 120 | 8 | 23.44 |  | 3352.8 | 31.75 | 3048 | 203.2 | 595.376
|  | 1.63 | 120 | 8 | 23.25 |  |  | 41.402 | 3048 | 203.2 | 590.55
| O.D | "T" | "R1" | "R2" | IDD | ASME | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.63 | 132 | 8.38 | 23.94 |  |  | 16.002 | 3352.8 | 212.852 | 608.076
|  | 1 | 132 | 8.38 | 23.75 |  | 138" | 25.4 | 3352.8 | 212.852 | 603.25
|  | 1.38 | 132 | 8.38 | 23.56 |  | 3505.2 | 35.052 | 3352.8 | 212.852 | 598.424
|  | 1.75 | 132 | 8.38 | 23.38 |  |  | 44.45 | 3352.8 | 212.852 | 593.852
|  | 0.63 | 132 | 8.75 | 25.88 |  |  | 16.002 | 3352.8 | 222.25 | 657.352
|  | 1 | 132 | 8.75 | 25.63 |  | 144" | 25.4 | 3352.8 | 222.25 | 651.002
|  | 1.38 | 132 | 8.75 | 25.44 |  | 3657.6 | 35.052 | 3352.8 | 222.25 | 646.176
|  | 1.75 | 132 | 8.75 | 25.19 |  |  | 44.45 | 3352.8 | 222.25 | 639.826
|  | 0.75 | 144 | 9.38 | 27.75 |  |  | 19.05 | 3657.6 | 238.252 | 704.85
|  | 1.13 | 144 | 9.38 | 27.5 |  | 156" | 28.702 | 3657.6 | 238.252 | 698.5
|  | 1.5 | 144 | 9.38 | 27.31 |  | 3962.4 | 38.1 | 3657.6 | 238.252 | 693.674
|  | 1.88 | 144 | 9.38 | 27.06 |  |  | 47.752 | 3657.6 | 238.252 | 687.324
|  | 0.75 | 144 | 10.13 | 31.81 |  |  | 19.05 | 3657.6 | 257.302 | 807.974
|  | 1.13 | 144 | 10.13 | 31.5 |  | 168" | 28.702 | 3657.6 | 257.302 | 800.1
|  | 1.5 | 144 | 10.13 | 31.31 |  | 4267.2 | 38.1 | 3657.6 | 257.302 | 795.274
|  | 1.88 | 144 | 10.13 | 31.13 |  |  | 47.752 | 3657.6 | 257.302 | 790.702
|  | 0.88 | 170 | 10.88 | 31.44 |  |  | 22.352 | 4318 | 276.352 | 798.576
|  | 1.25 | 170 | 10.88 | 31.25 |  | 180 | 31.75 | 4318 | 276.352 | 793.75
|  | 1.63 | 170 | 10.88 | 31 |  | 4572 | 41.402 | 4318 | 276.352 | 787.4
|  | 2 | 170 | 10.88 | 30.81 |  |  | 50.8 | 4318 | 276.352 | 782.574
|  | 0.88 | 170 | 11.63 | 35.44 |  |  | 22.352 | 4318 | 295.402 | 900.176
|  | 1.25 | 170 | 11.63 | 35.19 |  | 192" | 31.75 | 4318 | 295.402 | 893.826
|  | 1.63 | 170 | 11.63 | 34.94 |  | 4876.8 | 41.402 | 4318 | 295.402 | 887.476
|  | 2 | 170 | 11.63 | 34.75 |  |  | 50.8 | 4318 | 295.402 | 882.65
| O.D | "T" | "R1" | "R2" | IDD | ASME | O.D | "T" (mm) | "R1"(mm) | "R2"(mm) | IDD(mm)
|  | 0.88 | 170 | 12.25 | 39.56 |  |  | 22.352 | 4318 | 311.15 | 1004.824
|  | 1.25 | 170 | 12.25 | 39.38 |  | 204" | 31.75 | 4318 | 311.15 | 1000.252
|  | 1.63 | 170 | 12.25 | 39.19 |  | 5181.6 | 41.402 | 4318 | 311.15 | 995.426
|  | 2 | 170 | 12.25 | 38.94 |  |  | 50.8 | 4318 | 311.15 | 989.076
|  | 1 | 170 | 12.63 | 41.81 |  |  | 25.4 | 4318 | 320.802 | 1061.974
|  | 1.38 | 170 | 12.63 | 41.63 |  | 210" | 35.052 | 4318 | 320.802 | 1057.402
|  | 1.75 | 170 | 12.63 | 41.31 |  | 5334 | 44.45 | 4318 | 320.802 | 1049.274
|  | 2.25 | 170 | 12.63 | 41 |  |  | 57.15 | 4318 | 320.802 | 1041.4
|  | 1 | 170 | 13 | 44.25 |  |  | 25.4 | 4318 | 330.2 | 1123.95
|  | 1.38 | 170 | 13 | 44 |  | 216" | 35.052 | 4318 | 330.2 | 1117.6
|  | 1.75 | 170 | 13 | 43.69 |  | 5486.4 | 44.45 | 4318 | 330.2 | 1109.726
|  | 2 | 170 | 13 | 43.5 |  |  | 50.8 | 4318 | 330.2 | 1104.9
|  | 1 | 180 | 13.75 | 46.56 |  |  | 25.4 | 4572 | 349.25 | 1182.624
|  | 1.38 | 180 | 13.75 | 46.31 |  | 228" | 35.052 | 4572 | 349.25 | 1176.274
|  | 1.75 | 180 | 13.75 | 46.06 |  | 5791.2 | 44.45 | 4572 | 349.25 | 1169.924
|  | 2 | 180 | 13.75 | 45.69 |  |  | 50.8 | 4572 | 349.25 | 1160.526
Key In I.D. Inches
Tangent Line
Straight
Flange
Varies
2" Nom.
51mm
2:1 Elliptical Head
Tangent Line
Straight
Flange
Varies
2" Nom.
51mm
Wall Thickness "T"
Knuckle Radius
"R2"
Dish Radius
"R1"
Area for nozzle attachment
O.D. - (R2+T)x2
Outside Diameter (O.D.)
Flanged and Dished Head
Inside Depth
of Dish
"IDD"
26"
28"
30"
32"
34"
36"
38"
40"
42"
48"
54"
60"
66"
72"
78"
84"
90"
96"
102"
108"
114"
120"
126"
132"
138"
144"
156"
168"
180"
192"
204"
216"
228"
240"
Tangent Line
Straight
Flange
Varies
2" Nom.
51mm
Wall Thickness "T"
Knuckle Radius
"R2"
Dish Radius
"R1"
Area for nozzle attachment
O.D. - (R2+T)x2
Outside Diameter (O.D.)
Flanged and Dished Head (ASME)
Inside Depth
of Dish
"IDD"
26"
28"
30"
32"
34"
36"
38"
40"
42"
48"
54"
60"
66"
72"
78"
84"
90"
96"
102"
108"
114"
120"
126"
132"
138"
144"
156"
168"
180"
192"
204"
210"
216"
228"
Note on G24: CELLIS: Enter ID in Inches

## Pipe Spans
Based on using carbon steel pipe (A53-GR B) filled with water
Spans are based on insulated and uninsulated lines below 650 Deg. F
Nom. |  | Wall | Alowable
Pipe | Pipe | Thickness | Span | Deflection
Size | Sch. | Inches | Ft- In (mm) | Inches (mm) | Ft- In (mm) | Ft- In (mm)
3/4" | 80 | 0.154 | 10'-0" (3048) | 3/8" (10) | 7'-0" (2134) | 8'-0" (2438)
1" | 80 | 0.179 | 13'-0" (3962) | 1/2" (13) | 9'-0" (2743) | 10'-0" (3048)
1-1/2" | 80 | 0.2 | 17'-0" (5182) | 3/4" (19) | 11'-0" (3353) | 13'-0" (3962)
2" | 40 | 0.154 | 19'-0" (5791) | 1" (25) | 12'-0" (3658) | 14'-0" (4267)
2" | 80 | 0.218 | 20'-0" (6096) | 1" (25) | 13'-0" (3962) | 15'-0" (4572)
3" | 40 | 0.216 | 25'-0" (7620) | 1" (25) | 16'-0" (4877) | 18'-0" (5486)
4" | 40 | 0.237 | 27'-0" (8230) | 1" (25) | 18'-0" (5486) | 20'-0" (6096)
6" | 40 | 0.28 | 33'-0" (10058) | 1" (25) | 22'-0" (6706) | 25'-0" (7620)
8" | 30 | 0.277 | 36'-0" (10973) | 1" (25) | 24'-0" (7315) | 27'-0" (8230)
10" | 20 | 0.25 | 38'-0" (11582) | 1" (25) | 25'-0" (7620) | 29'-0" (8839)
10" | 40 | 0.365 | 41'-0" (12497) | 1" (25) | 27'-0" (8230) | 31'-0" (9449)
12" | 20 | 0.25 | 40'-0" (12192) | 1" (25) | 26'-0" (7925) | 30'-0" (9144)
12" | Std | 0.375 | 44'-0" (13411) | 1" (25) | 29'-0" (8839) | 33'-0" (10058)
14" | 10 | 0.25 | 42'-0" (12802) | 1" (25) | 27'-0" (8230) | 31'-0" (9449)
14" | Std | 0.375 | 46'-0" (14021) | 1" (25) | 30'-0" (9144) | 34'-0" (10363)
16" | 10 | 0.25 | 44'-0" (13411) | 1" (25) | 28'-0" (8534) | 33'-0" (10058)
16" | Std | 0.375 | 48'-0" (14630) | 1" (25) | 31'-0" (9449) | 36'-0" (10973)
18" | 10 | 0.25 | 45'-0" (13716) | 1" (25) | 29'-0" (8839) | 34'-0" (10363)
18" | Std | 0.375 | 50'-0" (15240) | 1" (25) | 33'-0" (10058) | 38'-0" (11582)
20" | 10 | 0.25 | 47'-0" (14326) | 1" (25) | 31'-0" (9449) | 36'-0" (10973)
20" | 20 | 0.375 | 52'-0" (15850) | 1" (25) | 34'-0" (10363) | 39'-0" (11887)
24" | 10 | 0.25 | 49'-0" (14935) | 1" (25) | 32'-0" (9754) | 37'-0" (11278)
24" | 20 | 0.375 | 55'-0" (16764) | 1" (25) | 36'-0" (10973) | 41'-0" (12497)
ALLOWABLE PIPING SPANS

## ELL's
English Units
Nom. |  |  |  |  | Wall Thickness INCHES | [15 empty] | F
Pipe | Pipe | Light | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | A | B | K | D | V | E | INCHES |  | G
Size | O.D. | Wall | 20 | 30 | Std | 40 | 60 | X-Stg. | 80 | 100 | 120 | 140 | 160 | XX-Stg | IN | IN | IN | IN | IN | IN | ASA | MSS | IN
0.5 | 0.84 | 0.083 |  |  | 0.109 | 0.109 |  | 0.147 | 0.147 |  |  |  | 0.188 | 0.294 | 1.5 | 0.625 | 1.875 |  |  | 1 | 3 | 2 | 1.375
0.75 | 1.05 | 0.083 |  |  | 0.113 | 0.113 |  | 0.154 | 0.154 |  |  |  | 0.219 | 0.308 | 1.125 | 0.4375 | 1.6875 |  |  | 1 | 3 | 2 | 1.6875
1 | 1.315 | 0.109 |  |  | 0.133 | 0.133 |  | 0.179 | 0.179 |  |  |  | 0.25 | 0.358 | 1.5 | 0.875 | 2.1875 | 1 | 1.625 | 1.5 | 4 | 2 | 2
1.25 | 1.66 | 0.109 |  |  | 0.14 | 0.14 |  | 0.191 | 0.191 |  |  |  | 0.25 | 0.382 | 1.875 | 1 | 2.75 | 1.25 | 2 1/16 | 1.5 | 4 | 2 | 2.5
1.5 | 1.9 | 0.109 |  |  | 0.145 | 0.145 |  | 0.2 | 0.2 |  |  |  | 0.281 | 0.4 | 2.25 | 1.125 | 3.25 | 1.5 | 2 7/16 | 1.5 | 4 | 2 | 2.875
2 | 2.375 | 0.109 |  |  | 0.154 | 0.154 |  | 0.218 | 0.218 |  |  |  | 0.344 | 0.436 | 3 | 1.375 | 4.1875 | 2 | 3 3/16 | 1.5 | 6 | 2.5 | 3.625
2.5 | 2.875 | 0.12 |  |  | 0.203 | 0.203 |  | 0.276 | 0.276 |  |  |  | 0.375 | 0.552 | 3.75 | 1.75 | 5.1875 | 2.5 | 3 15/16 | 1.5 | 6 | 2.5 | 4.125
3 | 3.5 |  |  |  | 0.216 | 0.216 |  | 0.3 | 0.3 |  |  |  | 0.438 | 0.6 | 4.5 | 2 | 6.25 | 3 | 4.75 | 2 | 6 | 2.5 | 5
3.5 | 4 |  |  |  | 0.226 | 0.226 |  | 0.318 | 0.318 |  |  |  |  | 0.636 | 5.25 | 2.25 | 7.25 | 3.5 | 5.5 | 2.5 | 6 | 3 | 5.5
4 | 4.5 |  |  |  | 0.237 | 0.237 |  | 0.337 | 0.337 |  | 0.438 |  | 0.531 | 0.674 | 6 | 2.5 | 8.25 | 4 | 6.25 | 2.5 | 6 | 3 | 6 3/16
5 | 5.563 |  |  |  | 0.258 | 0.258 |  | 0.375 | 0.375 |  | 0.5 |  | 0.625 | 0.75 | 7.5 | 3.125 | 10.3125 | 5 | 7.75 | 3 | 8 | 3 | 7 5/16
6 | 6.625 |  |  |  | 0.28 | 0.28 |  | 0.432 | 0.432 |  | 0.562 |  | 0.719 | 0.864 | 9 | 3.75 | 12.3125 | 6 | 9 5/16 | 3.5 | 8 | 3.5 | 8.5
8 | 8.625 |  | 0.25 | 0.277 | 0.322 | 0.322 | 0.406 | 0.5 | 0.5 | 0.594 | 0.719 | 0.812 | 0.906 | 0.875 | 12 | 5 | 16.3125 | 8 | 12 5/16 | 4 | 8 | 4 | 10.625
10 | 10.75 |  | 0.25 | 0.307 | 0.365 | 0.365 | 0.5 | 0.5 | 0.594 | 0.719 | 0.844 | 1 | 1.125 | 1 | 15 | 6.25 | 20.375 | 10 | 15.375 | 5 | 10 | 5 | 12.75
12 | 12.75 |  | 0.25 | 0.33 | 0.375 | 0.406 | 0.562 | 0.5 | 0.688 | 0.844 | 1 | 1.125 | 1.312 | 1 | 18 | 7.5 | 24.375 | 12 | 18.375 | 6 | 10 | 6 | 15
14 | 14 |  | 0.312 | 0.375 | 0.375 | 0.438 | 0.594 | 0.5 | 0.75 | 0.938 | 1.094 | 1.25 | 1.406 |  | 21 | 8.75 | 28 | 14 | 21 | 6.5 | 12 |  | 16.25
16 | 16 |  | 0.312 | 0.375 | 0.375 | 0.5 | 0.656 | 0.5 | 0.844 | 1.031 | 1.219 | 1.438 | 1.594 |  | 24 | 10 | 32 | 16 | 24 | 7 | 12 |  | 18.5
18 | 18 |  | 0.312 | 0.438 | 0.375 | 0.562 | 0.75 | 0.5 | 0.938 | 1.156 | 1.375 | 1.562 | 1.781 |  | 27 | 11.25 | 36 | 18 | 27 | 8 | 12 |  | 21
20 | 20 |  | 0.375 | 0.5 | 0.375 | 0.594 | 0.812 | 0.5 | 1.031 | 1.281 | 1.5 | 1.75 | 1.969 |  | 30 | 12.5 | 40 | 20 | 30 | 9 | 12 |  | 23
24 | 24 |  | 0.375 | 0.562 | 0.375 | 0.688 | 0.969 | 0.5 | 1.219 | 1.531 | 1.812 | 2.062 | 2.344 |  | 36 | 15 | 48 | 24 | 36 | 10.5 | 12 |  | 27.25
30 | 30 |  | 0.5 | 0.625 | 0.375 |  |  | 0.5 | [6 empty] | 45 | 18.5 | 60 | 30 | 45 | 10.5
36 | 36 |  | 0.5 | 0.625 | 0.375 | 0.75 |  | 0.5 | [6 empty] | 54 | 22.25 |  | 36 | 54 | 10.5
42 | 42 |  |  |  | 0.375 |  |  | 0.5 | [6 empty] | 63 | 26 |  | 42 |  | 12
48 | 48 |  |  |  | 0.375 |  |  | 0.5 | [6 empty] | 72 | 29.75 |  | 48 |  | 13.5
Metric Units
Nom. |  |  |  |  | Wall Thickness millimeters | [15 empty] | F
Pipe | Pipe | Light | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | Sch. | A | B | K | D | V | E | millimeters |  | G
Size | O.D. | Wall | 20 | 30 | Std | 40 | 60 | X-Stg. | 80 | 100 | 120 | 140 | 160 | XX-Stg | mm | mm | mm | mm | mm | mm | ASA | MSS | mm
12.7 | 21.336 | 2.1082 |  |  | 2.7686 | 2.7686 |  | 3.7338 | 3.7338 |  |  |  | 4.7752 | 7.4676 | 38.1 | 15.875 | 47.625 |  |  | 25.4 | 76.2 | 50.8 | 34.925
19.05 | 26.67 | 2.1082 |  |  | 2.8702 | 2.8702 |  | 3.9116 | 3.9116 |  |  |  | 5.5626 | 7.8232 | 28.575 | 11.1125 | 42.8625 |  |  | 25.4 | 76.2 | 50.8 | 42.8625
25.4 | 33.401 | 2.7686 |  |  | 3.3782 | 3.3782 |  | 4.5466 | 4.5466 |  |  |  | 6.35 | 9.0932 | 38.1 | 22.225 | 55.5625 | 25.4 | 41.275 | 38.1 | 101.6 | 50.8 | 50.8
31.75 | 42.164 | 2.7686 |  |  | 3.556 | 3.556 |  | 4.8514 | 4.8514 |  |  |  | 6.35 | 9.7028 | 47.625 | 25.4 | 69.85 | 31.75 | 52.3875 | 38.1 | 101.6 | 50.8 | 63.5
38.1 | 48.26 | 2.7686 |  |  | 3.683 | 3.683 |  | 5.08 | 5.08 |  |  |  | 7.1374 | 10.16 | 57.15 | 28.575 | 82.55 | 38.1 | 61.9125 | 38.1 | 101.6 | 50.8 | 73.025
50.8 | 60.325 | 2.7686 |  |  | 3.9116 | 3.9116 |  | 5.5372 | 5.5372 |  |  |  | 8.7376 | 11.0744 | 76.2 | 34.925 | 106.3625 | 50.8 | 80.9625 | 38.1 | 152.4 | 63.5 | 92.075
63.5 | 73.025 | 3.048 |  |  | 5.1562 | 5.1562 |  | 7.0104 | 7.0104 |  |  |  | 9.525 | 14.0208 | 95.25 | 44.45 | 131.7625 | 63.5 | 100.0125 | 38.1 | 152.4 | 63.5 | 104.775
76.2 | 88.9 |  |  |  | 5.4864 | 5.4864 |  | 7.62 | 7.62 |  |  |  | 11.1252 | 15.24 | 114.3 | 50.8 | 158.75 | 76.2 | 120.65 | 50.8 | 152.4 | 63.5 | 127
88.9 | 101.6 |  |  |  | 5.7404 | 5.7404 |  | 8.0772 | 8.0772 |  |  |  |  | 16.1544 | 133.35 | 57.15 | 184.15 | 88.9 | 139.7 | 63.5 | 152.4 | 76.2 | 139.7
101.6 | 114.3 |  |  |  | 6.0198 | 6.0198 |  | 8.5598 | 8.5598 |  | 11.1252 |  | 13.4874 | 17.1196 | 152.4 | 63.5 | 209.55 | 101.6 | 158.75 | 63.5 | 152.4 | 76.2 | 157.1625
127 | 141.3002 |  |  |  | 6.5532 | 6.5532 |  | 9.525 | 9.525 |  | 12.7 |  | 15.875 | 19.05 | 190.5 | 79.375 | 261.9375 | 127 | 196.85 | 76.2 | 203.2 | 76.2 | 185.7375
152.4 | 168.275 |  |  |  | 7.112 | 7.112 |  | 10.9728 | 10.9728 |  | 14.2748 |  | 18.2626 | 21.9456 | 228.6 | 95.25 | 312.7375 | 152.4 | 236.5375 | 88.9 | 203.2 | 88.9 | 215.9
203.2 | 219.075 |  | 6.35 | 7.0358 | 8.1788 | 8.1788 | 10.3124 | 12.7 | 12.7 | 15.0876 | 18.2626 | 20.6248 | 23.0124 | 22.225 | 304.8 | 127 | 414.3375 | 203.2 | 312.7375 | 101.6 | 203.2 | 101.6 | 269.875
254 | 273.05 |  | 6.35 | 7.7978 | 9.271 | 9.271 | 12.7 | 12.7 | 15.0876 | 18.2626 | 21.4376 | 25.4 | 28.575 | 25.4 | 381 | 158.75 | 517.525 | 254 | 390.525 | 127 | 254 | 127 | 323.85
304.8 | 323.85 |  | 6.35 | 8.382 | 9.525 | 10.3124 | 14.2748 | 12.7 | 17.4752 | 21.4376 | 25.4 | 28.575 | 33.3248 | 25.4 | 457.2 | 190.5 | 619.125 | 304.8 | 466.725 | 152.4 | 254 | 152.4 | 381
355.6 | 355.6 |  | 7.9248 | 9.525 | 9.525 | 11.1252 | 15.0876 | 12.7 | 19.05 | 23.8252 | 27.7876 | 31.75 | 35.7124 |  | 533.4 | 222.25 | 711.2 | 355.6 | 533.4 | 165.1 | 304.8 |  | 412.75
406.4 | 406.4 |  | 7.9248 | 9.525 | 9.525 | 12.7 | 16.6624 | 12.7 | 21.4376 | 26.1874 | 30.9626 | 36.5252 | 40.4876 |  | 609.6 | 254 | 812.8 | 406.4 | 609.6 | 177.8 | 304.8 |  | 469.9
457.2 | 457.2 |  | 7.9248 | 11.1252 | 9.525 | 14.2748 | 19.05 | 12.7 | 23.8252 | 29.3624 | 34.925 | 39.6748 | 45.2374 |  | 685.8 | 285.75 | 914.4 | 457.2 | 685.8 | 203.2 | 304.8 |  | 533.4
508 | 508 |  | 9.525 | 12.7 | 9.525 | 15.0876 | 20.6248 | 12.7 | 26.1874 | 32.5374 | 38.1 | 44.45 | 50.0126 |  | 762 | 317.5 | 1016 | 508 | 762 | 228.6 | 304.8 |  | 584.2
609.6 | 609.6 |  | 9.525 | 14.2748 | 9.525 | 17.4752 | 24.6126 | 12.7 | 30.9626 | 38.8874 | 46.0248 | 52.3748 | 59.5376 |  | 914.4 | 381 | 1219.2 | 609.6 | 914.4 | 266.7 | 304.8 |  | 692.15
762 | 762 |  | 12.7 | 15.875 | 9.525 |  |  | 12.7 | [6 empty] | 1143 | 469.9 | 1524 | 762 | 1143 | 266.7
914.4 | 914.4 |  | 12.7 | 15.875 | 9.525 | 19.05 |  | 12.7 | [6 empty] | 1371.6 | 565.15 |  | 914.4 | 1371.6 | 266.7
1066.8 | 1066.8 |  |  |  | 9.525 |  |  | 12.7 | [6 empty] | 1600.2 | 660.4 |  | 1066.8 |  | 304.8
1219.2 | 1219.2 |  |  |  | 9.525 |  |  | 12.7 | [6 empty] | 1828.8 | 755.65 |  | 1219.2 |  | 342.9
A
A
90 L.R. ELL.
90 Red. L.R. ELL
B
B
45 L.R. ELL.
K
A
A
180 L.R. ELL
D
D
90 S.R. ELL
D
D
V
180 S.R. ELL
E
CAP
G
F
LAP JOINT
STUB END

## Tee's & Reducers
English Units
Nom. |  |  |  |  | Nom. |  |  |  |  | Nom. |  |  |  |  | Nom.
Pipe | Outlet | C | M | H | Pipe | Outlet | C | M | H | Pipe | Outlet | C | M | H | Pipe | Outlet | C | M | H
Size |  |  |  |  | Size |  |  |  |  | Size |  |  |  |  | Size
IN | IN | IN | IN | IN | IN | IN | IN | IN | IN | IN | IN | IN | IN | IN | IN | IN | IN | IN | IN
0.75 | 0.75 | 1.125 |  |  | 3.5 | 3.5 | 3.75 |  |  | 10 | 10 | 8.5 |  |  | 20 | 20 | 15
0.75 | 0.5 | 1.125 | 1.125 | 1.5 | ¦ | 3 | 3.75 | 3.625 | 4 | ¦ | 8 | 8.5 | 8 | 7 | ¦ | 18 | 15 | 14.5 | 20
1 | 1 | 1.5 |  |  | ¦ | 2.5 | 3.75 | 3.5 | 4 | ¦ | 6 | 8.5 | 7.625 | 7 | ¦ | 16 | 15 | 14 | 20
1 | 0.75 | 1.5 | 1.5 | 2 | ¦ | 2 | 3.75 | 3.25 | 4 | ¦ | 5 | 8.5 | 7.5 | 7 | ¦ | 14 | 15 | 14 | 20
1 | 0.5 | 1.5 | 1.5 | 2 | 3.5 | 1.5 | 3.75 | 3.125 | 4 | 10 | 4 | 8.5 | 7.25 | 7 | ¦ | 12 | 15 | 13.625 | 20
1.25 | 1.25 | 1.875 |  |  | 4 | 4 | 4.125 |  |  | 12 | 12 | 10 |  |  | ¦ | 10 | 15 | 13.125 | 20
¦ | 1 | 1.875 | 1.875 | 2 | ¦ | 3.5 | 4.125 | 4 | 4 | ¦ | 10 | 10 | 9.5 | 8 | 20 | 8 | 15 | 12.75 | 20
¦ | 0.75 | 1.875 | 1.875 | 2 | ¦ | 3 | 4.125 | 3.875 | 4 | ¦ | 8 | 10 | 9 | 8 | 24 | 24 | 17
1.25 | 0.5 | 1.875 | 1.875 | 2 | ¦ | 2.5 | 4.125 | 3.75 | 4 | ¦ | 6 | 10 | 8.625 | 8 | ¦ | 20 | 17 | 17 | 20
1.5 | 1.5 | 2.25 |  |  | ¦ | 2 | 4.125 | 3.5 | 4 | 12 | 5 | 10 | 8.5 | 8 | ¦ | 18 | 17 | 16.5 | 20
¦ | 1.25 | 2.25 | 2.25 | 2.5 | 4 | 1.5 | 4.125 | 3.375 | 4 | 14 | 14 | 11 |  |  | ¦ | 16 | 17 | 16 | 20
¦ | 1 | 2.25 | 2.25 | 2.5 | 5 | 5 | 4.875 |  |  | ¦ | 12 | 11 | 10.625 | 13 | ¦ | 14 | 17 | 16 | 20
¦ | 0.75 | 2.25 | 2.25 | 2.5 | ¦ | 4 | 4.875 | 4.625 | 5 | ¦ | 10 | 11 | 10.125 | 13 | ¦ | 12 | 17 | 15.625 | 20
1.5 | 0.5 | 2.25 | 2.25 | 2.5 | ¦ | 3.5 | 4.875 | 4.5 | 5 | ¦ | 8 | 11 | 9.75 | 13 | 24 | 10 | 17 | 15.125 | 20
2 | 2 | 2.5 |  |  | ¦ | 3 | 4.875 | 4.375 | 5 | 14 | 6 | 11 | 9.375 | 13 | 30 | 30 | 22
¦ | 1.5 | 2.5 | 2.375 | 3 | ¦ | 2.5 | 4.875 | 4.25 | 5 | 16 | 16 | 12 |  |  | ¦ | 24 | 22 | 21 | 24
¦ | 1.25 | 2.5 | 2.25 | 3 | 5 | 2 | 4.875 | 4.125 | 5 | ¦ | 14 | 12 | 12 | 14 | ¦ | 20 | 22 | 20 | 24
¦ | 1 | 2.5 | 2 | 3 | 6 | 6 | 5.625 |  |  | ¦ | 12 | 12 | 11.625 | 14 | ¦ | 18 | 22 | 19.5 | 24
2 | 0.75 | 2.5 | 1.75 | 3 | ¦ | 5 | 5.625 | 5.375 | 5.5 | ¦ | 10 | 12 | 11.125 | 14 | ¦ | 16 | 22 | 19 | 24
2.5 | 2.5 | 3 |  |  | ¦ | 4 | 5.625 | 5.125 | 5.5 | ¦ | 8 | 12 | 10.75 | 14 | 30 | 14 | 22 | 19 | 24
¦ | 2 | 3 | 2.75 | 3.5 | ¦ | 3.5 | 5.625 | 5 | 5.5 | 16 | 6 | 12 | 10.375 | 14 | 36 | 36 | 26.5
¦ | 1.5 | 3 | 2.625 | 3.5 | ¦ | 3 | 5.625 | 4.875 | 5.5 | 18 | 18 | 13.5 |  |  | ¦ | 30 | 26.5 | 25 | 24
¦ | 1.25 | 3 | 2.5 | 3.5 | 6 | 2.5 | 5.625 | 4.75 | 5.5 | ¦ | 16 | 13.5 | 13 | 15 | ¦ | 24 | 26.5 | 24 | 24
2.5 | 1 | 3 | 2.25 | 3.5 | 8 | 8 | 7 |  |  | ¦ | 14 | 13.5 | 13 | 15 | ¦ | 20 | 26.5 | 23 | 24
3 | 3 | 3.375 |  |  | ¦ | 6 | 7 | 6.625 | 6 | ¦ | 12 | 13.5 | 12.625 | 15 | ¦ | 18 | 26.5 | 22.5 | 24
¦ | 2.5 | 3.375 | 3.25 | 3.5 | ¦ | 5 | 7 | 6.375 | 6 | ¦ | 10 | 13.5 | 12.125 | 15 | 36 | 16 | 26.5 | 22 | 24
¦ | 2 | 3.375 | 3 | 3.5 | ¦ | 4 | 7 | 6.125 | 6 | 18 | 8 | 13.5 | 11.75 | 15 | 42 | 42 | 30 | 28
¦ | 1.5 | 3.375 | 2.875 | 3.5 | 8 | 3.5 | 7 | 6 | 6 | [5 empty] | ¦ | 36 | 30 | 28 | 24
3 | 1.25 | 3.375 | 2.75 | 3.5 | [10 empty] | ¦ | 30 | 30 | 28 | 24
[15 empty] | ¦ | 24 | 30 | 26 | 24
[15 empty] | 42 | 20 | 30 | 26 | 24
[15 empty] | 48 | 48 | 35 | 33
[15 empty] | ¦ | 42 | 35 | 32 | 28
[15 empty] | ¦ | 36 | 35 | 31 | 28
[15 empty] | 48 | 30 | 35 | 30 | 28
Metric Units
Nom. |  |  |  |  | Nom. |  |  |  |  | Nom. |  |  |  |  | Nom.
Pipe | Outlet | C | M | H | Pipe | Outlet | C | M | H | Pipe | Outlet | C | M | H | Pipe | Outlet | C | M | H
Size |  |  |  |  | Size |  |  |  |  | Size |  |  |  |  | Size
mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm
19.05 | 19.05 | 28.575 |  |  | 88.9 | 88.9 | 95.25 |  |  | 254 | 254 | 215.9 |  |  | 508 | 508 | 381
19.05 | 12.7 | 28.575 | 28.575 | 38.1 | ¦ | 76.2 | 95.25 | 92.075 | 101.6 | ¦ | 203.2 | 215.9 | 203.2 | 177.8 | ¦ | 457.2 | 381 | 368.3 | 508
25.4 | 25.4 | 38.1 |  |  | ¦ | 63.5 | 95.25 | 88.9 | 101.6 | ¦ | 152.4 | 215.9 | 193.675 | 177.8 | ¦ | 406.4 | 381 | 355.6 | 508
25.4 | 19.05 | 38.1 | 38.1 | 50.8 | ¦ | 50.8 | 95.25 | 82.55 | 101.6 | ¦ | 127 | 215.9 | 190.5 | 177.8 | ¦ | 355.6 | 381 | 355.6 | 508
25.4 | 12.7 | 38.1 | 38.1 | 50.8 | 88.9 | 38.1 | 95.25 | 79.375 | 101.6 | 254 | 101.6 | 215.9 | 184.15 | 177.8 | ¦ | 304.8 | 381 | 346.075 | 508
31.75 | 31.75 | 47.625 |  |  | 101.6 | 101.6 | 104.775 |  |  | 304.8 | 304.8 | 254 |  |  | ¦ | 254 | 381 | 333.375 | 508
¦ | 25.4 | 47.625 | 47.625 | 50.8 | ¦ | 88.9 | 104.775 | 101.6 | 101.6 | ¦ | 254 | 254 | 241.3 | 203.2 | 508 | 203.2 | 381 | 323.85 | 508
¦ | 19.05 | 47.625 | 47.625 | 50.8 | ¦ | 76.2 | 104.775 | 98.425 | 101.6 | ¦ | 203.2 | 254 | 228.6 | 203.2 | 609.6 | 609.6 | 431.8
31.75 | 12.7 | 47.625 | 47.625 | 50.8 | ¦ | 63.5 | 104.775 | 95.25 | 101.6 | ¦ | 152.4 | 254 | 219.075 | 203.2 | ¦ | 508 | 431.8 | 431.8 | 508
38.1 | 38.1 | 57.15 |  |  | ¦ | 50.8 | 104.775 | 88.9 | 101.6 | 304.8 | 127 | 254 | 215.9 | 203.2 | ¦ | 457.2 | 431.8 | 419.1 | 508
¦ | 31.75 | 57.15 | 57.15 | 63.5 | 101.6 | 38.1 | 104.775 | 85.725 | 101.6 | 355.6 | 355.6 | 279.4 |  |  | ¦ | 406.4 | 431.8 | 406.4 | 508
¦ | 25.4 | 57.15 | 57.15 | 63.5 | 127 | 127 | 123.825 |  |  | ¦ | 304.8 | 279.4 | 269.875 | 330.2 | ¦ | 355.6 | 431.8 | 406.4 | 508
¦ | 19.05 | 57.15 | 57.15 | 63.5 | ¦ | 101.6 | 123.825 | 117.475 | 127 | ¦ | 254 | 279.4 | 257.175 | 330.2 | ¦ | 304.8 | 431.8 | 396.875 | 508
38.1 | 12.7 | 57.15 | 57.15 | 63.5 | ¦ | 88.9 | 123.825 | 114.3 | 127 | ¦ | 203.2 | 279.4 | 247.65 | 330.2 | 609.6 | 254 | 431.8 | 384.175 | 508
50.8 | 50.8 | 63.5 |  |  | ¦ | 76.2 | 123.825 | 111.125 | 127 | 355.6 | 152.4 | 279.4 | 238.125 | 330.2 | 762 | 762 | 558.8
¦ | 38.1 | 63.5 | 60.325 | 76.2 | ¦ | 63.5 | 123.825 | 107.95 | 127 | 406.4 | 406.4 | 304.8 |  |  | ¦ | 609.6 | 558.8 | 533.4 | 609.6
¦ | 31.75 | 63.5 | 57.15 | 76.2 | 127 | 50.8 | 123.825 | 104.775 | 127 | ¦ | 355.6 | 304.8 | 304.8 | 355.6 | ¦ | 508 | 558.8 | 508 | 609.6
¦ | 25.4 | 63.5 | 50.8 | 76.2 | 152.4 | 152.4 | 142.875 |  |  | ¦ | 304.8 | 304.8 | 295.275 | 355.6 | ¦ | 457.2 | 558.8 | 495.3 | 609.6
50.8 | 19.05 | 63.5 | 44.45 | 76.2 | ¦ | 127 | 142.875 | 136.525 | 139.7 | ¦ | 254 | 304.8 | 282.575 | 355.6 | ¦ | 406.4 | 558.8 | 482.6 | 609.6
63.5 | 63.5 | 76.2 |  |  | ¦ | 101.6 | 142.875 | 130.175 | 139.7 | ¦ | 203.2 | 304.8 | 273.05 | 355.6 | 762 | 355.6 | 558.8 | 482.6 | 609.6
¦ | 50.8 | 76.2 | 69.85 | 88.9 | ¦ | 88.9 | 142.875 | 127 | 139.7 | 406.4 | 152.4 | 304.8 | 263.525 | 355.6 | 914.4 | 914.4 | 673.1
¦ | 38.1 | 76.2 | 66.675 | 88.9 | ¦ | 76.2 | 142.875 | 123.825 | 139.7 | 457.2 | 457.2 | 342.9 |  |  | ¦ | 762 | 673.1 | 635 | 609.6
¦ | 31.75 | 76.2 | 63.5 | 88.9 | 152.4 | 63.5 | 142.875 | 120.65 | 139.7 | ¦ | 406.4 | 342.9 | 330.2 | 381 | ¦ | 609.6 | 673.1 | 609.6 | 609.6
63.5 | 25.4 | 76.2 | 57.15 | 88.9 | 203.2 | 203.2 | 177.8 |  |  | ¦ | 355.6 | 342.9 | 330.2 | 381 | ¦ | 508 | 673.1 | 584.2 | 609.6
76.2 | 76.2 | 85.725 |  |  | ¦ | 152.4 | 177.8 | 168.275 | 152.4 | ¦ | 304.8 | 342.9 | 320.675 | 381 | ¦ | 457.2 | 673.1 | 571.5 | 609.6
¦ | 63.5 | 85.725 | 82.55 | 88.9 | ¦ | 127 | 177.8 | 161.925 | 152.4 | ¦ | 254 | 342.9 | 307.975 | 381 | 914.4 | 406.4 | 673.1 | 558.8 | 609.6
¦ | 50.8 | 85.725 | 76.2 | 88.9 | ¦ | 101.6 | 177.8 | 155.575 | 152.4 | 457.2 | 203.2 | 342.9 | 298.45 | 381 | 1066.8 | 1066.8 | 762 | 711.2
¦ | 38.1 | 85.725 | 73.025 | 88.9 | 203.2 | 88.9 | 177.8 | 152.4 | 152.4 | [5 empty] | ¦ | 914.4 | 762 | 711.2 | 609.6
76.2 | 31.75 | 85.725 | 69.85 | 88.9 | [10 empty] | ¦ | 762 | 762 | 711.2 | 609.6
[15 empty] | ¦ | 609.6 | 762 | 660.4 | 609.6
[15 empty] | 1066.8 | 508 | 762 | 660.4 | 609.6
[15 empty] | 1219.2 | 1219.2 | 889 | 838.2
[15 empty] | ¦ | 1066.8 | 889 | 812.8 | 711.2
[15 empty] | ¦ | 914.4 | 889 | 787.4 | 711.2
[15 empty] | 1219.2 | 762 | 889 | 762 | 711.2
C
C
C
Straight Tee
C
C
M
Reducing Tee
H
H
Conc. Reducer
Eccentric Reducer
C
C
C
Straight Tee
C
C
M
Reducing Tee
H
H
Conc. Reducer
Eccentric Reducer

## Flanges
|  |  | 150 LB. FLANGES - INCHES | [7 empty] | 150 LB. FLANGES - MILLIMETERS
Nom. |  |  |  | Y |  |  | No. & | Nom. |  |  |  | Y |  |  | No. &
Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of | Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of
Size | INCHES | INCHES | Neck | Thrd. | Joint | Circle | Holes | Size | mm | mm | Neck | Thrd. | Joint | Circle | Holes
0.5 | 3.5 | 0.4375 | 1.875 | 0.625 | 0.625 | 2.375 | 4 - 5/8 | 12.7 | 88.9 | 11.1125 | 47.625 | 15.875 | 15.875 | 60.325 | 4 - 16
0.75 | 3.875 | 0.5 | 2.0625 | 0.625 | 0.625 | 2.75 | 4 - 5/8 | 19.05 | 98.425 | 12.7 | 52.3875 | 15.875 | 15.875 | 69.85 | 4 - 16
1 | 4.25 | 0.5625 | 2.1875 | 0.6875 | 0.6875 | 3.125 | 4 - 5/8 | 25.4 | 107.95 | 14.2875 | 55.5625 | 17.4625 | 17.4625 | 79.375 | 4 - 16
1.25 | 4.625 | 0.625 | 2.25 | 0.8125 | 0.8125 | 3.5 | 4 - 5/8 | 31.75 | 117.475 | 15.875 | 57.15 | 20.6375 | 20.6375 | 88.9 | 4 - 16
1.5 | 5 | 0.6875 | 2.4375 | 0.875 | 0.875 | 3.875 | 4 - 5/8 | 38.1 | 127 | 17.4625 | 61.9125 | 22.225 | 22.225 | 98.425 | 4 - 16
2 | 6 | 0.75 | 2.5 | 1 | 1 | 4.75 | 4-3/4 | 50.8 | 152.4 | 19.05 | 63.5 | 25.4 | 25.4 | 120.65 | 4-19
2.5 | 7 | 0.875 | 2.75 | 1.125 | 1.125 | 5.5 | 4-3/4 | 63.5 | 177.8 | 22.225 | 69.85 | 28.575 | 28.575 | 139.7 | 4-19
3 | 7.5 | 0.9375 | 2.75 | 1.1875 | 1.1875 | 6 | 4-3/4 | 76.2 | 190.5 | 23.8125 | 69.85 | 30.1625 | 30.1625 | 152.4 | 4-19
3.5 | 8.5 | 0.9375 | 2.8125 | 1.25 | 1.25 | 7 | 8-3/4 | 88.9 | 215.9 | 23.8125 | 71.4375 | 31.75 | 31.75 | 177.8 | 8-19
4 | 9 | 0.9375 | 3 | 1.3125 | 1.3125 | 7.5 | 8-3/4 | 101.6 | 228.6 | 23.8125 | 76.2 | 33.3375 | 33.3375 | 190.5 | 8-19
5 | 10 | 0.9375 | 3.5 | 1.4375 | 1.4375 | 8.5 | 8-7/8 | 127 | 254 | 23.8125 | 88.9 | 36.5125 | 36.5125 | 215.9 | 8-22
6 | 11 | 1 | 3.5 | 1.5625 | 1.5625 | 9.5 | 8-7/8 | 152.4 | 279.4 | 25.4 | 88.9 | 39.6875 | 39.6875 | 241.3 | 8-22
8 | 13.5 | 1.125 | 4 | 1.75 | 1.75 | 11.75 | 8-7/8 | 203.2 | 342.9 | 28.575 | 101.6 | 44.45 | 44.45 | 298.45 | 8-22
10 | 16 | 1.1875 | 4 | 1.9375 | 1.9375 | 14.25 | 12-1 | 254 | 406.4 | 30.1625 | 101.6 | 49.2125 | 49.2125 | 361.95 | 12-25
12 | 19 | 1.25 | 4.5 | 2.1875 | 2.1875 | 17 | 12-1 | 304.8 | 482.6 | 31.75 | 114.3 | 55.5625 | 55.5625 | 431.8 | 12-25
14 | 21 | 1.375 | 5 | 2.25 | 3.125 | 18.75 | 12-1 1/8 | 355.6 | 533.4 | 34.925 | 127 | 57.15 | 79.375 | 476.25 | 12-29
16 | 23.5 | 1.4375 | 5 | 2.5 | 3.4375 | 21.25 | 16-1 1/8 | 406.4 | 596.9 | 36.5125 | 127 | 63.5 | 87.3125 | 539.75 | 16-29
18 | 25 | 1.5625 | 5.5 | 2.6875 | 3.8125 | 22.75 | 16-1 1/4 | 457.2 | 635 | 39.6875 | 139.7 | 68.2625 | 96.8375 | 577.85 | 16-32
20 | 27.5 | 1.6875 | 5.6875 | 2.875 | 4.0625 | 25 | 20-1 1/4 | 508 | 698.5 | 42.8625 | 144.4625 | 73.025 | 103.1875 | 635 | 20-32
24 | 32 | 1.875 | 6 | 3.25 | 4.375 | 29.5 | 20-1 3/8 | 609.6 | 812.8 | 47.625 | 152.4 | 82.55 | 111.125 | 749.3 | 20-35
|  |  | 300 LB. FLANGES - INCHES | [7 empty] | 300 LB. FLANGES - MILLIMETERS
Nom. |  |  |  | Y |  |  | No. & | Nom. |  |  |  | Y |  |  | No. &
Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of | Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of
Size | INCHES | INCHES | Neck | Thrd. | Joint | Circle | Holes | Size | mm | mm | Neck | Thrd. | Joint | Circle | Holes
0.5 | 3.75 | 0.5625 | 2.0625 | 0.875 | 0.875 | 2.625 | 4 - 5/8 | 12.7 | 95.25 | 14.2875 | 52.3875 | 22.225 | 22.225 | 66.675 | 4 - 16
0.75 | 4.625 | 0.625 | 2.25 | 1 | 1 | 3.25 | 4 - 3/4 | 19.05 | 117.475 | 15.875 | 57.15 | 25.4 | 25.4 | 82.55 | 4 - 19
1 | 4.875 | 0.6875 | 2.4375 | 1.0625 | 1.0625 | 3.5 | 4 - 3/4 | 25.4 | 123.825 | 17.4625 | 61.9125 | 26.9875 | 26.9875 | 88.9 | 4 - 19
1.25 | 5.25 | 0.75 | 2.5625 | 1.0625 | 1.0625 | 3.875 | 4 - 3/4 | 31.75 | 133.35 | 19.05 | 65.0875 | 26.9875 | 26.9875 | 98.425 | 4 - 19
1.5 | 6.125 | 0.8125 | 2.6875 | 1.1875 | 1.1875 | 4.5 | 4 -7/8 | 38.1 | 155.575 | 20.6375 | 68.2625 | 30.1625 | 30.1625 | 114.3 | 4 -22
2 | 6.5 | 0.875 | 2.75 | 1.3125 | 1.3125 | 5 | 8-3/4 | 50.8 | 165.1 | 22.225 | 69.85 | 33.3375 | 33.3375 | 127 | 8-19
2.5 | 7.5 | 1 | 3 | 1.5 | 1.5 | 5.875 | 8-7/8 | 63.5 | 190.5 | 25.4 | 76.2 | 38.1 | 38.1 | 149.225 | 8-22
3 | 8.25 | 1.125 | 3.125 | 1.6875 | 1.6875 | 6.625 | 8-7/8 | 76.2 | 209.55 | 28.575 | 79.375 | 42.8625 | 42.8625 | 168.275 | 8-22
3.5 | 9 | 1.1875 | 3.1875 | 1.75 | 1.75 | 7.25 | 8-7/8 | 88.9 | 228.6 | 30.1625 | 80.9625 | 44.45 | 44.45 | 184.15 | 8-22
4 | 10 | 1.25 | 3.375 | 1.875 | 1.875 | 7.875 | 8-7/8 | 101.6 | 254 | 31.75 | 85.725 | 47.625 | 47.625 | 200.025 | 8-22
5 | 11 | 1.375 | 3.875 | 2 | 2 | 9.25 | 8-7/8 | 127 | 279.4 | 34.925 | 98.425 | 50.8 | 50.8 | 234.95 | 8-22
6 | 12.5 | 1.4375 | 3.875 | 2.0625 | 2.0625 | 10.625 | 12-7/8 | 152.4 | 317.5 | 36.5125 | 98.425 | 52.3875 | 52.3875 | 269.875 | 12-22
8 | 15 | 1.625 | 4.375 | 2.4375 | 2.4375 | 13 | 12-1 | 203.2 | 381 | 41.275 | 111.125 | 61.9125 | 61.9125 | 330.2 | 12-25
10 | 17.5 | 1.875 | 4.625 | 2.625 | 3.75 | 15.25 | 16-1 1/8 | 254 | 444.5 | 47.625 | 117.475 | 66.675 | 95.25 | 387.35 | 16-29
12 | 20.5 | 2 | 5.125 | 2.875 | 4 | 17.75 | 16-1 1/4 | 304.8 | 520.7 | 50.8 | 130.175 | 73.025 | 101.6 | 450.85 | 16-32
14 | 23 | 2.125 | 5.625 | 3 | 4.375 | 20.25 | 20-1 1/4 | 355.6 | 584.2 | 53.975 | 142.875 | 76.2 | 111.125 | 514.35 | 20-32
16 | 25.5 | 2.25 | 5.75 | 3.25 | 4.75 | 22.5 | 20-1 3/8 | 406.4 | 647.7 | 57.15 | 146.05 | 82.55 | 120.65 | 571.5 | 20-35
18 | 28 | 2.375 | 6.25 | 3.5 | 5.125 | 24.75 | 24-1 3/8 | 457.2 | 711.2 | 60.325 | 158.75 | 88.9 | 130.175 | 628.65 | 24-35
20 | 30.5 | 2.5 | 6.375 | 3.75 | 5.5 | 27 | 24-1 3/8 | 508 | 774.7 | 63.5 | 161.925 | 95.25 | 139.7 | 685.8 | 24-35
24 | 36 | 2.75 | 6.625 | 4.1875 | 6 | 32 | 24-1 5/8 | 609.6 | 914.4 | 69.85 | 168.275 | 106.3625 | 152.4 | 812.8 | 24-41
** The 1/4" raised face is not included in the thickness "Y" or "C" | [7 empty] | ** The 6mm raised face is not included in the thickness "Y" or "C"
|  |  | 400 LB. FLANGES - INCHES | [7 empty] | 400 LB. FLANGES - MILLIMETERS
Nom. |  |  | **Y (See Note Above) |  |  |  | No. & | Nom. |  |  | **Y (See Note Above) |  |  |  | No. &
Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of | Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of
Size | INCHES | INCHES | Neck | Thrd. | Joint | Circle | Holes | Size | mm | mm | Neck | Thrd. | Joint | Circle | Holes
0.5 | 3.75 | 0.5625 | 2.0625 | 0.875 | 0.875 | 2.625 | 4 - 5/8 | 12.7 | 95.25 | 14.2875 | 52.3875 | 22.225 | 22.225 | 66.675 | 4 - 16
0.75 | 4.625 | 0.625 | 2.25 | 1 | 1 | 3.25 | 4 - 3/4 | 19.05 | 117.475 | 15.875 | 57.15 | 25.4 | 25.4 | 82.55 | 4 - 19
1 | 4.875 | 0.6875 | 2.4375 | 1.0625 | 1.0625 | 3.5 | 4 - 3/4 | 25.4 | 123.825 | 17.4625 | 61.9125 | 26.9875 | 26.9875 | 88.9 | 4 - 19
1.25 | 5.25 | 0.8125 | 2.625 | 1.125 | 1.125 | 3.875 | 4 - 3/4 | 31.75 | 133.35 | 20.6375 | 66.675 | 28.575 | 28.575 | 98.425 | 4 - 19
1.5 | 6.125 | 0.875 | 2.75 | 1.25 | 1.25 | 4.5 | 4 -7/8 | 38.1 | 155.575 | 22.225 | 69.85 | 31.75 | 31.75 | 114.3 | 4 -22
2 | 6.5 | 1 | 2.875 | 1.4375 | 1.4375 | 5 | 8-3/4 | 50.8 | 165.1 | 25.4 | 73.025 | 36.5125 | 36.5125 | 127 | 8-19
2.5 | 7.5 | 1.125 | 3.125 | 1.625 | 1.625 | 5.875 | 8-7/8 | 63.5 | 190.5 | 28.575 | 79.375 | 41.275 | 41.275 | 149.225 | 8-22
3 | 8.25 | 1.25 | 3.25 | 1.8125 | 1.8125 | 6.625 | 8-7/8 | 76.2 | 209.55 | 31.75 | 82.55 | 46.0375 | 46.0375 | 168.275 | 8-22
3.5 | 9 | 1.375 | 3.625 | 1.9375 | 1.9375 | 7.25 | 8-1 | 88.9 | 228.6 | 34.925 | 92.075 | 49.2125 | 49.2125 | 184.15 | 8-25
4 | 10 | 1.375 | 3.5 | 2 | 2 | 7.875 | 8-1 | 101.6 | 254 | 34.925 | 88.9 | 50.8 | 50.8 | 200.025 | 8-25
5 | 11 | 1.5 | 4 | 2.125 | 2.125 | 9.25 | 8-1 | 127 | 279.4 | 38.1 | 101.6 | 53.975 | 53.975 | 234.95 | 8-25
6 | 12.5 | 1.625 | 4.0625 | 2.25 | 2.25 | 10.625 | 12-1 | 152.4 | 317.5 | 41.275 | 103.1875 | 57.15 | 57.15 | 269.875 | 12-25
8 | 15 | 1.875 | 4.625 | 2.6875 | 2.6875 | 13 | 12-1 1/8 | 203.2 | 381 | 47.625 | 117.475 | 68.2625 | 68.2625 | 330.2 | 12-29
10 | 17.5 | 2.125 | 4.875 | 2.875 | 4 | 15.25 | 16-1 1/4 | 254 | 444.5 | 53.975 | 123.825 | 73.025 | 101.6 | 387.35 | 16-32
12 | 20.5 | 2.25 | 5.375 | 3.125 | 4.25 | 17.75 | 16-1 3/8 | 304.8 | 520.7 | 57.15 | 136.525 | 79.375 | 107.95 | 450.85 | 16-35
14 | 23 | 2.375 | 5.875 | 3.3125 | 4.625 | 20.25 | 20-1 3/8 | 355.6 | 584.2 | 60.325 | 149.225 | 84.1375 | 117.475 | 514.35 | 20-35
16 | 25.5 | 2.5 | 6 | 3.6875 | 5 | 22.5 | 20-1 1/2 | 406.4 | 647.7 | 63.5 | 152.4 | 93.6625 | 127 | 571.5 | 20-38
18 | 28 | 2.625 | 6.5 | 3.875 | 5.375 | 24.75 | 24-1 1/2 | 457.2 | 711.2 | 66.675 | 165.1 | 98.425 | 136.525 | 628.65 | 24-38
20 | 30.5 | 2.75 | 6.625 | 4 | 5.75 | 27 | 24-1 5/8 | 508 | 774.7 | 69.85 | 168.275 | 101.6 | 146.05 | 685.8 | 24-41
24 | 36 | 3 | 6.875 | 4.5 | 6.25 | 32 | 24-1 7/8 | 609.6 | 914.4 | 76.2 | 174.625 | 114.3 | 158.75 | 812.8 | 24-48
** The 1/4" raised face is not included in the thickness "Y" or "C" | [7 empty] | ** The 6mm raised face is not included in the thickness "Y" or "C"
|  |  | 600 LB. FLANGES - INCHES | [7 empty] | 600 LB. FLANGES - MILLIMETERS
Nom. |  |  | **Y (See Note Above) |  |  |  | No. & | Nom. |  |  | **Y (See Note Above) |  |  |  | No. &
Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of | Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of
Size | INCHES | INCHES | Neck | Thrd. | Joint | Circle | Holes | Size | mm | mm | Neck | Thrd. | Joint | Circle | Holes
0.5 | 3.75 | 0.5625 | 2.0625 | 0.875 | 0.875 | 2.625 | 4 - 5/8 | 12.7 | 95.25 | 14.2875 | 52.3875 | 22.225 | 22.225 | 66.675 | 4 - 16
0.75 | 4.625 | 0.625 | 2.25 | 1 | 1 | 6.25 | 4 - 3/4 | 19.05 | 117.475 | 15.875 | 57.15 | 25.4 | 25.4 | 158.75 | 4 - 19
1 | 4.875 | 0.6875 | 2.4375 | 1.0625 | 1.0625 | 3.5 | 4 - 3/4 | 25.4 | 123.825 | 17.4625 | 61.9125 | 26.9875 | 26.9875 | 88.9 | 4 - 19
1.25 | 5.25 | 0.8125 | 2.625 | 1.125 | 1.125 | 3.875 | 4 - 3/4 | 31.75 | 133.35 | 20.6375 | 66.675 | 28.575 | 28.575 | 98.425 | 4 - 19
1.5 | 6.125 | 0.875 | 2.75 | 1.25 | 1.25 | 4.5 | 4 -7/8 | 38.1 | 155.575 | 22.225 | 69.85 | 31.75 | 31.75 | 114.3 | 4 -22
2 | 6.5 | 1 | 2.875 | 1.4375 | 1.4375 | 5 | 8-3/4 | 50.8 | 165.1 | 25.4 | 73.025 | 36.5125 | 36.5125 | 127 | 8-19
2.5 | 7.5 | 1.125 | 3.125 | 1.625 | 1.625 | 5.875 | 8-7/8 | 63.5 | 190.5 | 28.575 | 79.375 | 41.275 | 41.275 | 149.225 | 8-22
3 | 8.25 | 1.25 | 3.25 | 1.8125 | 1.8125 | 6.625 | 8-7/8 | 76.2 | 209.55 | 31.75 | 82.55 | 46.0375 | 46.0375 | 168.275 | 8-22
3.5 | 9 | 1.375 | 3.375 | 1.9375 | 1.9375 | 7.25 | 8-1 | 88.9 | 228.6 | 34.925 | 85.725 | 49.2125 | 49.2125 | 184.15 | 8-25
4 | 10.75 | 1.5 | 4 | 2.125 | 2.125 | 8.5 | 8-1 | 101.6 | 273.05 | 38.1 | 101.6 | 53.975 | 53.975 | 215.9 | 8-25
5 | 13 | 1.75 | 4.5 | 2.375 | 2.375 | 10.5 | 8-1 1/8 | 127 | 330.2 | 44.45 | 114.3 | 60.325 | 60.325 | 266.7 | 8-29
6 | 14 | 1.875 | 4.625 | 2.625 | 2.625 | 11.5 | 12-1 1/8 | 152.4 | 355.6 | 47.625 | 117.475 | 66.675 | 66.675 | 292.1 | 12-29
8 | 16.5 | 2.1875 | 5.25 | 3 | 3 | 13.75 | 12-1 1/4 | 203.2 | 419.1 | 55.5625 | 133.35 | 76.2 | 76.2 | 349.25 | 12-32
10 | 20 | 2.5 | 6 | 3.375 | 4.375 | 17 | 16-1 3/8 | 254 | 508 | 63.5 | 152.4 | 85.725 | 111.125 | 431.8 | 16-35
12 | 22 | 2.625 | 6.125 | 3.625 | 4.625 | 19.25 | 20-1 3/8 | 304.8 | 558.8 | 66.675 | 155.575 | 92.075 | 117.475 | 488.95 | 20-35
14 | 23.75 | 2.75 | 6.5 | 3.6875 | 5 | 20.75 | 20-1 1/2 | 355.6 | 603.25 | 69.85 | 165.1 | 93.6625 | 127 | 527.05 | 20-38
16 | 27 | 3 | 7 | 4.1875 | 5.5 | 23.75 | 20-1 5/8 | 406.4 | 685.8 | 76.2 | 177.8 | 106.3625 | 139.7 | 603.25 | 20-41
18 | 29.25 | 3.25 | 7.25 | 4.625 | 6 | 25.75 | 20-1 3/4 | 457.2 | 742.95 | 82.55 | 184.15 | 117.475 | 152.4 | 654.05 | 20-44
20 | 32 | 3.5 | 7.5 | 5 | 6.5 | 28.5 | 24-1 3/4 | 508 | 812.8 | 88.9 | 190.5 | 127 | 165.1 | 723.9 | 24-44
24 | 37 | 4 | 8 | 5.5 | 7.25 | 33 | 24-2 | 609.6 | 939.8 | 101.6 | 203.2 | 139.7 | 184.15 | 838.2 | 24-51
** The 1/4" raised face is not included in the thickness "Y" or "C" | [7 empty] | ** The 6mm raised face is not included in the thickness "Y" or "C"
|  |  | 900 LB. FLANGES - INCHES | [7 empty] | 900 LB. FLANGES - MILLIMETERS
Nom. |  |  | **Y (See Note Above) |  |  |  | No. & | Nom. |  |  | **Y (See Note Above) |  |  |  | No. &
Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of | Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of
Size | INCHES | INCHES | Neck | Thrd. | Joint | Circle | Holes | Size | mm | mm | Neck | Thrd. | Joint | Circle | Holes
0.5 | 4.75 | 0.875 | 2.375 | 1.25 | 1.25 | 3.25 | 4 - 7/8 | 12.7 | 120.65 | 22.225 | 60.325 | 31.75 | 31.75 | 82.55 | 4 - 22
0.75 | 5.125 | 1 | 2.75 | 1.375 | 1.375 | 3.5 | 4 - 7/8 | 19.05 | 130.175 | 25.4 | 69.85 | 34.925 | 34.925 | 88.9 | 4 -22
1 | 5.875 | 1.125 | 2.875 | 1.625 | 1.625 | 4 | 4 - 1 | 25.4 | 149.225 | 28.575 | 73.025 | 41.275 | 41.275 | 101.6 | 4 - 25
1.25 | 6.25 | 1.125 | 2.875 | 1.625 | 1.625 | 4.375 | 4 - 1 | 31.75 | 158.75 | 28.575 | 73.025 | 41.275 | 41.275 | 111.125 | 4 - 25
1.5 | 7 | 1.25 | 3.25 | 1.75 | 1.75 | 4.875 | 4 -1 1/8 | 38.1 | 177.8 | 31.75 | 82.55 | 44.45 | 44.45 | 123.825 | 4 -29
2 | 8.5 | 1.5 | 4 | 2.25 | 2.25 | 6.5 | 8-1 | 50.8 | 215.9 | 38.1 | 101.6 | 57.15 | 57.15 | 165.1 | 8-25
2.5 | 9.625 | 1.625 | 4.125 | 2.5 | 2.5 | 7.5 | 8-1 1/8 | 63.5 | 244.475 | 41.275 | 104.775 | 63.5 | 63.5 | 190.5 | 8-29
3 | 9.5 | 1.5 | 4 | 2.125 | 2.125 | 7.5 | 8-1 | 76.2 | 241.3 | 38.1 | 101.6 | 53.975 | 53.975 | 190.5 | 8-25
3.5 | [7 empty] | 88.9
4 | 11.5 | 1.75 | 4.5 | 2.75 | 2.75 | 9.25 | 8-1 1/4 | 101.6 | 292.1 | 44.45 | 114.3 | 69.85 | 69.85 | 234.95 | 8-32
5 | 13.75 | 2 | 5 | 3.125 | 3.125 | 11 | 8-1 3/8 | 127 | 349.25 | 50.8 | 127 | 79.375 | 79.375 | 279.4 | 8-35
6 | 15 | 2.1875 | 5.5 | 3.375 | 3.375 | 12.5 | 12-1 1/4 | 152.4 | 381 | 55.5625 | 139.7 | 85.725 | 85.725 | 317.5 | 12-32
8 | 18.5 | 2.5 | 6.375 | 4 | 4.5 | 15.5 | 12-1 1/2 | 203.2 | 469.9 | 63.5 | 161.925 | 101.6 | 114.3 | 393.7 | 12-38
10 | 21.5 | 2.75 | 7.25 | 4.25 | 5 | 18.5 | 16-1 1/2 | 254 | 546.1 | 69.85 | 184.15 | 107.95 | 127 | 469.9 | 16-38
12 | 24 | 3.125 | 7.875 | 4.625 | 5.625 | 21 | 20-1 1/2 | 304.8 | 609.6 | 79.375 | 200.025 | 117.475 | 142.875 | 533.4 | 20-38
14 | 25.25 | 3.375 | 8.375 | 5.125 | 6.125 | 22 | 20-1 5/8 | 355.6 | 641.35 | 85.725 | 212.725 | 130.175 | 155.575 | 558.8 | 20-41
16 | 27.75 | 3.5 | 8.5 | 5.25 | 6.5 | 24.25 | 20-1 3/4 | 406.4 | 704.85 | 88.9 | 215.9 | 133.35 | 165.1 | 615.95 | 20-44
18 | 31 | 4 | 9 | 6 | 7.5 | 27 | 20-2 | 457.2 | 787.4 | 101.6 | 228.6 | 152.4 | 190.5 | 685.8 | 20-51
20 | 33.75 | 4.25 | 9.75 | 6.25 | 8.25 | 29.5 | 24-2 1/8 | 508 | 857.25 | 107.95 | 247.65 | 158.75 | 209.55 | 749.3 | 24-54
24 | 41 | 5.5 | 11.5 | 8 | 10.5 | 35.5 | 24-2 5/8 | 609.6 | 1041.4 | 139.7 | 292.1 | 203.2 | 266.7 | 901.7 | 24-67
** The 1/4" raised face is not included in the thickness "Y" or "C" | [7 empty] | ** The 6mm raised face is not included in the thickness "Y" or "C"
|  |  | 1500 LB. FLANGES - INCHES | [7 empty] | 1500 LB. FLANGES - MILLIMETERS
Nom. |  |  | **Y (See Note Above) |  |  |  | No. & | Nom. |  |  | **Y (See Note Above) |  |  |  | No. &
Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of | Pipe | O | C | Weld | Slip on | Lap | Bolt | Size of
Size | INCHES | INCHES | Neck | Thrd. | Joint | Circle | Holes | Size | mm | mm | Neck | Thrd. | Joint | Circle | Holes
0.5 | 4.75 | 0.875 | 2.375 | 1.25 | 1.25 | 3.25 | 4 - 7/8 | 12.7 | 120.65 | 22.225 | 60.325 | 31.75 | 31.75 | 82.55 | 4 - 22
0.75 | 5.125 | 1 | 2.75 | 1.375 | 1.375 | 3.5 | 4 - 7/8 | 19.05 | 130.175 | 25.4 | 69.85 | 34.925 | 34.925 | 88.9 | 4 -22
1 | 5.875 | 1.125 | 2.875 | 1.625 | 1.625 | 4 | 4 - 1 | 25.4 | 149.225 | 28.575 | 73.025 | 41.275 | 41.275 | 101.6 | 4 - 25
1.25 | 6.25 | 1.125 | 2.875 | 1.625 | 1.625 | 4.375 | 4 - 1 | 31.75 | 158.75 | 28.575 | 73.025 | 41.275 | 41.275 | 111.125 | 4 - 25
1.5 | 7 | 1.25 | 3.25 | 1.75 | 1.75 | 4.875 | 4 -1 1/8 | 38.1 | 177.8 | 31.75 | 82.55 | 44.45 | 44.45 | 123.825 | 4 -29
2 | 8.5 | 1.5 | 4 | 2.25 | 2.25 | 6.5 | 8-1 | 50.8 | 215.9 | 38.1 | 101.6 | 57.15 | 57.15 | 165.1 | 8-25
2.5 | 9.625 | 1.625 | 4.125 | 2.5 | 2.5 | 7.5 | 8-1 1/8 | 63.5 | 244.475 | 41.275 | 104.775 | 63.5 | 63.5 | 190.5 | 8-29
3 | 10.5 | 1.875 | 4.625 | 2.875 | 2.875 | 8 | 8-1 1/4 | 76.2 | 266.7 | 47.625 | 117.475 | 73.025 | 73.025 | 203.2 | 8-32
3.5 | [7 empty] | 88.9
4 | 12.25 | 2.125 | 4.875 | 3.5625 | 3.5625 | 9.5 | 8-1 3/8 | 101.6 | 311.15 | 53.975 | 123.825 | 90.4875 | 90.4875 | 241.3 | 8-35
5 | 14.75 | 2.875 | 6.125 | 4.125 | 4.125 | 11.5 | 8-1 5/8 | 127 | 374.65 | 73.025 | 155.575 | 104.775 | 104.775 | 292.1 | 8-41
6 | 15.5 | 3.25 | 6.75 | 4.6875 | 4.6875 | 12.5 | 12-1 1/2 | 152.4 | 393.7 | 82.55 | 171.45 | 119.0625 | 119.0625 | 317.5 | 12-38
8 | 19 | 3.625 | 8.375 | 5.625 | 5.625 | 15.5 | 12-1 3/4 | 203.2 | 482.6 | 92.075 | 212.725 | 142.875 | 142.875 | 393.7 | 12-44
10 | 23 | 4.25 | 10 | 6.25 | 7 | 19 | 12-2 | 254 | 584.2 | 107.95 | 254 | 158.75 | 177.8 | 482.6 | 12-51
12 | 26.5 | 4.875 | 11.125 | 7.125 | 8.625 | 22.5 | 16-2 1/8 | 304.8 | 673.1 | 123.825 | 282.575 | 180.975 | 219.075 | 571.5 | 16-54
14 | 29.5 | 5.25 | 11.75 |  | 9.5 | 25 | 16-2 3/8 | 355.6 | 749.3 | 133.35 | 298.45 | 0 | 241.3 | 635 | 16-60
16 | 32.5 | 5.75 | 12.25 |  | 10.25 | 27.75 | 16 - 2 5/8 | 406.4 | 825.5 | 146.05 | 311.15 | 0 | 260.35 | 704.85 | 16 - 67
18 | 36 | 6.375 | 12.875 |  | 10.875 | 30.5 | 16- 2 7/8 | 457.2 | 914.4 | 161.925 | 327.025 | 0 | 276.225 | 774.7 | 16- 73
20 | 38.75 | 7 | 14 |  | 11.5 | 32.75 | 16-3 1/8 | 508 | 984.25 | 177.8 | 355.6 | 0 | 292.1 | 831.85 | 16-79
24 | 46 | 8 | 16 |  | 13 | 39 | 16 -3 5/8 | 609.6 | 1168.4 | 203.2 | 406.4 | 0 | 330.2 | 990.6 | 16 -92
O
Y
C
Weld Neck Flange
O
C
Y
Slip-On Flange
O
Y
C
Threaded Flange
O
C
Y
Lap Joint Flange
O
C
Blind Flange

## Flg Weights
150 # FLANGE WEIGHTS
|  | English | [5 empty] | Metric
Nom. | 150# | 150# | 150# | 150# | 150# | Nom. | 150# | 150# | 150# | 150# | 150#
Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG. | Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG.
Size | Wt. | Wt. | Wt. | Wt. | Wt. | Size | Wt. | Wt. | Wt. | Wt. | Wt.
Inches | Lbs | Lbs | Lbs | Lbs | Lbs | mm | Kg | Kg | Kg | Kg | Kg
0.5 | 2 | 1 | 1 | 1 | 2 | 12.7 | 0.90718 | 0.45359 | 0.45359 | 0.45359 | 0.90718
0.75 | 2 | 1.5 | 1.5 | 1.5 | 2 | 19.05 | 0.90718 | 0.68039 | 0.68039 | 0.68039 | 0.90718
1 | 2.5 | 2 | 2 | 2 | 2 | 25.4 | 1.134 | 0.90718 | 0.90718 | 0.90718 | 0.90718
1.25 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 31.75 | 1.134 | 1.134 | 1.134 | 1.134 | 1.3608
1.5 | 4 | 3 | 3 | 3 | 3 | 38.1 | 1.8144 | 1.3608 | 1.3608 | 1.3608 | 1.3608
2 | 6 | 5 | 5 | 5 | 4 | 63.5 | 2.7216 | 2.268 | 2.268 | 2.268 | 1.8144
2.5 | 10 | 8 | 8 | 8 | 7 | 63.5 | 4.5359 | 3.6287 | 3.6287 | 3.6287 | 3.1751
3 | 11.5 | 9 | 10 | 9 | 9 | 76.2 | 5.2163 | 4.0823 | 4.5359 | 4.0823 | 4.0823
3.5 | 12 | 11 | 12 | 11 | 13 | 88.9 | 5.4431 | 4.9895 | 5.4431 | 4.9895 | 5.8967
4 | 16.5 | 13 | 13 | 12 | 17 | 101.6 | 7.4843 | 5.8967 | 5.8967 | 5.4431 | 7.7111
5 | 21 | 15 | 15 | 13 | 20 | 152.4 | 9.5254 | 6.8039 | 6.8039 | 5.8967 | 9.0718
6 | 26 | 17 | 19.5 | 18 | 27 | 152.4 | 11.7934 | 7.7111 | 8.8451 | 8.1647 | 12.247
8 | 42 | 28 | 30 | 28 | 47 | 203.2 | 19.0509 | 12.7006 | 13.6078 | 12.7006 | 21.3188
10 | 54 | 40 | 41 | 36 | 67 | 254 | 24.494 | 18.1437 | 18.5973 | 16.3293 | 30.3907
12 | 88 | 61 | 65 | 60 | 102 | 304.8 | 39.9161 | 27.6691 | 29.4835 | 27.2155 | 46.2664
14 | 114 | 83 | 85 | 77 | 139 | 406.4 | 51.7095 | 37.6482 | 38.5554 | 34.9266 | 63.0493
16 | 142 | 106 | 93 | 104 | 187 | 406.4 | 64.4101 | 48.0808 | 42.1841 | 47.1736 | 84.8218
18 | 165 | 109 | 120 | 146 | 217 | 457.2 | 74.8427 | 49.4416 | 54.4311 | 66.2245 | 98.4296
20 | 197 | 148 | 155 | 159 | 283 | 508 | 89.3577 | 67.1317 | 70.3068 | 72.1212 | 128.3666
24 | 268 | 204 | 210 | 195 | 415 | 609.6 | 121.5628 | 92.5328 | 95.2544 | 88.4505 | 188.2408
300 # FLANGE WEIGHTS
|  | English | [5 empty] | Metric
Nom. | 300# | 300# | 300# | 300# | 300# | Nom. | 300# | 300# | 300# | 300# | 300#
Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG. | Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG.
Size | Wt. | Wt. | Wt. | Wt. | Wt. | Size | Wt. | Wt. | Wt. | Wt. | Wt.
Inches | Lbs | Lbs | Lbs | Lbs | Lbs | mm | Kg | Kg | Kg | Kg | Kg
0.5 | 2 | 1.5 | 1.5 | 1.5 | 2 | 12.7 | 0.90718 | 0.68039 | 0.68039 | 0.68039 | 0.90718
0.75 | 3 | 2.5 | 2.5 | 2.5 | 3 | 19.05 | 1.3608 | 1.134 | 1.134 | 1.134 | 1.3608
1 | 4 | 3 | 3 | 3 | 4 | 25.4 | 1.8144 | 1.3608 | 1.3608 | 1.3608 | 1.8144
1.25 | 5 | 4.5 | 4.5 | 4.5 | 6 | 31.75 | 2.268 | 2.0412 | 2.0412 | 2.0412 | 2.7216
1.5 | 7 | 6.5 | 6.5 | 6.5 | 7 | 38.1 | 3.1751 | 2.9484 | 2.9484 | 2.9484 | 3.1751
2 | 8 | 7 | 7 | 7 | 8 | 63.5 | 3.6287 | 3.1751 | 3.1751 | 3.1751 | 3.6287
2.5 | 12 | 10 | 10 | 10 | 12 | 63.5 | 5.4431 | 4.5359 | 4.5359 | 4.5359 | 5.4431
3 | 18 | 13 | 14 | 14.5 | 16 | 76.2 | 8.1647 | 5.8967 | 6.3503 | 6.5771 | 7.2575
3.5 | 20 | 16 | 16 | 16 | 21 | 88.9 | 9.0718 | 7.2575 | 7.2575 | 7.2575 | 9.5254
4 | 26.5 | 23.5 | 24 | 24 | 28 | 101.6 | 12.0202 | 10.6594 | 10.8862 | 10.8862 | 12.7006
5 | 36 | 29 | 31 | 26 | 37 | 152.4 | 16.3293 | 13.1542 | 14.0614 | 11.7934 | 16.7829
6 | 45 | 36 | 36 | 38 | 48 | 152.4 | 20.4117 | 16.3293 | 16.3293 | 17.2365 | 21.7724
8 | 69 | 56 | 56 | 55 | 79 | 203.2 | 31.2979 | 25.4012 | 25.4012 | 24.9476 | 35.8338
10 | 100 | 77 | 80 | 88 | 122 | 254 | 45.3592 | 34.9266 | 36.2874 | 39.9161 | 55.3383
12 | 142 | 113 | 110 | 139 | 183 | 304.8 | 64.4101 | 51.2559 | 49.8952 | 63.0493 | 83.0074
14 | 206 | 159 | 164 | 184 | 241 | 406.4 | 93.44 | 72.1212 | 74.3892 | 83.461 | 109.3158
16 | 249 | 210 | 220 | 234 | 315 | 406.4 | 112.9445 | 95.2544 | 99.7903 | 106.1406 | 142.8816
18 | 306 | 253 | 280 | 305 | 414 | 457.2 | 138.7993 | 114.7589 | 127.0059 | 138.3457 | 187.7873
20 | 369 | 307 | 325 | 375 | 515 | 508 | 167.3756 | 139.2529 | 147.4175 | 170.0971 | 233.6001
24 | 519 | 490 | 490 | 530 | 800 | 609.6 | 235.4145 | 222.2603 | 222.2603 | 240.404 | 362.8739
400 # FLANGE WEIGHTS
|  | English | [5 empty] | Metric
Nom. | 400 # | 400 # | 400 # | 400 # | 400 # | Nom. | 400 # | 400 # | 400 # | 400 # | 400 #
Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG. | Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG.
Size | Wt. | Wt. | Wt. | Wt. | Wt. | Size | Wt. | Wt. | Wt. | Wt. | Wt.
Inches | Lbs | Lbs | Lbs | Lbs | Lbs | mm | Kg | Kg | Kg | Kg | Kg
0.5 | 3 | 2 | 2 | 2 | 2 | 12.7 | 1.3608 | 0.90718 | 0.90718 | 0.90718 | 0.90718
0.75 | 3.5 | 3 | 3 | 3 | 3 | 19.05 | 1.5876 | 1.3608 | 1.3608 | 1.3608 | 1.3608
1 | 4 | 3.5 | 3.5 | 3.5 | 4 | 25.4 | 1.8144 | 1.5876 | 1.5876 | 1.5876 | 1.8144
1.25 | 5.5 | 4.5 | 4.5 | 4.5 | 6 | 31.75 | 2.4948 | 2.0412 | 2.0412 | 2.0412 | 2.7216
1.5 | 8 | 6.5 | 6.5 | 6.5 | 8 | 38.1 | 3.6287 | 2.9484 | 2.9484 | 2.9484 | 3.6287
2 | 10 | 8 | 8 | 8 | 10 | 63.5 | 4.5359 | 3.6287 | 3.6287 | 3.6287 | 4.5359
2.5 | 14 | 12 | 12 | 11 | 15 | 63.5 | 6.3503 | 5.4431 | 5.4431 | 4.9895 | 6.8039
3 | 18 | 15 | 15 | 14 | 20 | 76.2 | 8.1647 | 6.8039 | 6.8039 | 6.3503 | 9.0718
3.5 | 26 | 21 | 21 | 20 | 29 | 88.9 | 11.7934 | 9.5254 | 9.5254 | 9.0718 | 13.1542
4 | 30 | 24 | 24 | 22 | 33 | 101.6 | 13.6078 | 10.8862 | 10.8862 | 9.979 | 14.9685
5 | 39 | 31 | 31 | 29 | 44 | 152.4 | 17.6901 | 14.0614 | 14.0614 | 13.1542 | 19.9581
6 | 49 | 39 | 39 | 37 | 61 | 152.4 | 22.226 | 17.6901 | 17.6901 | 16.7829 | 27.6691
8 | 78 | 63 | 63 | 59 | 100 | 203.2 | 35.3802 | 28.5763 | 28.5763 | 26.762 | 45.3592
10 | 110 | 91 | 91 | 95 | 155 | 254 | 49.8952 | 41.2769 | 41.2769 | 43.0913 | 70.3068
12 | 160 | 129 | 129 | 152 | 226 | 304.8 | 72.5748 | 58.5134 | 58.5134 | 68.946 | 102.5119
14 | 233 | 191 | 191 | 210 | 310 | 406.4 | 105.687 | 86.6361 | 86.6361 | 95.2544 | 140.6136
16 | 294 | 253 | 253 | 280 | 398 | 406.4 | 133.3562 | 114.7589 | 114.7589 | 127.0059 | 180.5298
18 | 260 | 310 | 310 | 345 | 502 | 457.2 | 117.934 | 140.6136 | 140.6136 | 156.4894 | 227.7034
20 | 445 | 378 | 378 | 420 | 621 | 508 | 201.8486 | 171.4579 | 171.4579 | 190.5088 | 281.6809
24 | 640 | 539 | 539 | 615 | 936 | 609.6 | 290.2991 | 244.4863 | 244.4863 | 278.9593 | 424.5625
600 # FLANGE WEIGHTS
|  | English | [5 empty] | Metric
Nom. | 600 # | 600 # | 600 # | 600 # | 600 # | Nom. | 600 # | 600 # | 600 # | 600 # | 600 #
Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG. | Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG.
Size | Wt. | Wt. | Wt. | Wt. | Wt. | Size | Wt. | Wt. | Wt. | Wt. | Wt.
Inches | Lbs | Lbs | Lbs | Lbs | Lbs | mm | Kg | Kg | Kg | Kg | Kg
0.5 | 3 | 2 | 2 | 2 | 2 | 12.7 | 1.3608 | 0.90718 | 0.90718 | 0.90718 | 0.90718
0.75 | 3.5 | 3 | 3 | 3 | 3 | 19.05 | 1.5876 | 1.3608 | 1.3608 | 1.3608 | 1.3608
1 | 4 | 3.5 | 3.5 | 3.5 | 4 | 25.4 | 1.8144 | 1.5876 | 1.5876 | 1.5876 | 1.8144
1.25 | 5.5 | 4.5 | 4.5 | 4.5 | 6 | 31.75 | 2.4948 | 2.0412 | 2.0412 | 2.0412 | 2.7216
1.5 | 8 | 6.5 | 6.5 | 6.5 | 8 | 38.1 | 3.6287 | 2.9484 | 2.9484 | 2.9484 | 3.6287
2 | 10 | 8 | 8 | 8 | 10 | 63.5 | 4.5359 | 3.6287 | 3.6287 | 3.6287 | 4.5359
2.5 | 14 | 12 | 12 | 11 | 15 | 63.5 | 6.3503 | 5.4431 | 5.4431 | 4.9895 | 6.8039
3 | 18 | 15 | 15 | 14 | 20 | 76.2 | 8.1647 | 6.8039 | 6.8039 | 6.3503 | 9.0718
3.5 | 26 | 21 | 21 | 20 | 29 | 88.9 | 11.7934 | 9.5254 | 9.5254 | 9.0718 | 13.1542
4 | 37 | 33 | 33 | 31 | 41 | 101.6 | 16.7829 | 14.9685 | 14.9685 | 14.0614 | 18.5973
5 | 68 | 56 | 63 | 63 | 68 | 152.4 | 30.8443 | 25.4012 | 28.5763 | 28.5763 | 30.8443
6 | 73 | 66 | 80 | 78 | 86 | 152.4 | 33.1122 | 29.9371 | 36.2874 | 35.3802 | 39.0089
8 | 112 | 97 | 97 | 112 | 139 | 203.2 | 50.8023 | 43.9985 | 43.9985 | 50.8023 | 63.0493
10 | 189 | 177 | 177 | 195 | 231 | 254 | 85.729 | 80.2859 | 80.2859 | 88.4505 | 104.7798
12 | 226 | 215 | 215 | 240 | 295 | 304.8 | 102.5119 | 97.5224 | 97.5224 | 108.8622 | 133.8098
14 | 268 | 259 | 259 | 290 | 378 | 406.4 | 121.5628 | 117.4804 | 117.4804 | 131.5418 | 171.4579
16 | 481 | 366 | 366 | 400 | 527 | 406.4 | 218.1779 | 166.0148 | 166.0148 | 181.437 | 239.0432
18 | 555 | 476 | 476 | 469 | 665 | 457.2 | 251.7438 | 215.91 | 215.91 | 212.7348 | 301.6389
20 | 690 | 612 | 612 | 604 | 855 | 508 | 312.9788 | 277.5985 | 277.5985 | 273.9698 | 387.8215
24 | 977 | 876 | 876 | 866 | 1175 | 609.6 | 443.1598 | 397.3469 | 397.3469 | 392.811 | 532.9711
900 # FLANGE WEIGHTS
|  | English | [5 empty] | Metric
Nom. | 900 # | 900 # | 900 # | 900 # | 900 # | Nom. | 900 # | 900 # | 900 # | 900 # | 900 #
Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG. | Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG.
Size | Wt. | Wt. | Wt. | Wt. | Wt. | Size | Wt. | Wt. | Wt. | Wt. | Wt.
Inches | Lbs | Lbs | Lbs | Lbs | Lbs | mm | Kg | Kg | Kg | Kg | Kg
0.5 | 7 | 6 | 6 | 6 | 4 | 12.7 | 3.1751 | 2.7216 | 2.7216 | 2.7216 | 1.8144
0.75 | 7 | 6 | 6 | 6 | 6 | 19.05 | 3.1751 | 2.7216 | 2.7216 | 2.7216 | 2.7216
1 | 8.5 | 7.5 | 7.5 | 7.5 | 9 | 25.4 | 3.8555 | 3.4019 | 3.4019 | 3.4019 | 4.0823
1.25 | 10 | 10 | 10 | 10 | 10 | 31.75 | 4.5359 | 4.5359 | 4.5359 | 4.5359 | 4.5359
1.5 | 14 | 14 | 14 | 14 | 14 | 38.1 | 6.3503 | 6.3503 | 6.3503 | 6.3503 | 6.3503
2 | 24 | 22 | 22 | 21 | 25 | 63.5 | 10.8862 | 9.979 | 9.979 | 9.5254 | 11.3398
2.5 | 36 | 36 | 36 | 29 | 35 | 63.5 | 16.3293 | 16.3293 | 16.3293 | 13.1542 | 15.8757
3 | 29 | 31 | 31 | 25 | 32 | 76.2 | 13.1542 | 14.0614 | 14.0614 | 11.3398 | 14.515
4 | 51 | 53 | 53 | 51 | 54 | 101.6 | 23.1332 | 24.0404 | 24.0404 | 23.1332 | 24.494
5 | 86 | 83 | 83 | 81 | 87 | 152.4 | 39.0089 | 37.6482 | 37.6482 | 36.741 | 39.4625
6 | 110 | 108 | 108 | 105 | 113 | 152.4 | 49.8952 | 48.988 | 48.988 | 47.6272 | 51.2559
8 | 187 | 172 | 172 | 188 | 197 | 203.2 | 84.8218 | 78.0179 | 78.0179 | 85.2754 | 89.3577
10 | 268 | 245 | 245 | 277 | 290 | 254 | 121.5628 | 111.1301 | 111.1301 | 125.6451 | 131.5418
12 | 372 | 326 | 326 | 371 | 413 | 304.8 | 168.7364 | 147.8711 | 147.8711 | 168.2828 | 187.3337
14 | 562 | 380 | 380 | 397 | 494 | 406.4 | 254.9189 | 172.3651 | 172.3651 | 180.0762 | 224.0746
16 | 685 | 459 | 459 | 488 | 619 | 406.4 | 310.7108 | 208.1989 | 208.1989 | 221.3531 | 280.7737
18 | 924 | 647 | 647 | 670 | 880 | 457.2 | 419.1194 | 293.4743 | 293.4743 | 303.9069 | 399.1613
20 | 1164 | 792 | 792 | 868 | 1107 | 508 | 527.9816 | 359.2452 | 359.2452 | 393.7182 | 502.1268
24 | 2107 | 1480 | 1480 | 1659 | 2099 | 609.6 | 955.7192 | 671.3168 | 671.3168 | 752.5098 | 952.0904
1500 # FLANGE WEIGHTS
|  | English | [5 empty] | Metric
Nom. | 1500 # | 1500 # | 1500 # | 1500 # | 1500 # | Nom. | 1500 # | 1500 # | 1500 # | 1500 # | 1500 #
Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG. | Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG.
Size | Wt. | Wt. | Wt. | Wt. | Wt. | Size | Wt. | Wt. | Wt. | Wt. | Wt.
Inches | Lbs | Lbs | Lbs | Lbs | Lbs | mm | Kg | Kg | Kg | Kg | Kg
0.5 | 7 | 6 | 6 | 6 | 7 | 12.7 | 3.1751 | 2.7216 | 2.7216 | 2.7216 | 3.1751
0.75 | 7 | 6 | 6 | 6 | 10 | 19.05 | 3.1751 | 2.7216 | 2.7216 | 2.7216 | 4.5359
1 | 8.5 | 7.5 | 7.5 | 7.5 | 12 | 25.4 | 3.8555 | 3.4019 | 3.4019 | 3.4019 | 5.4431
1.25 | 10 | 10 | 10 | 10 | 18 | 31.75 | 4.5359 | 4.5359 | 4.5359 | 4.5359 | 8.1647
1.5 | 14 | 14 | 14 | 14 | 25 | 38.1 | 6.3503 | 6.3503 | 6.3503 | 6.3503 | 11.3398
2 | 24 | 22 | 23 | 21 | 39 | 63.5 | 10.8862 | 9.979 | 10.4326 | 9.5254 | 17.6901
2.5 | 36 | 36 | 36 | 29 | 56 | 63.5 | 16.3293 | 16.3293 | 16.3293 | 13.1542 | 25.4012
3 | 48 | 48 | 48 | 38 | 86 | 76.2 | 21.7724 | 21.7724 | 21.7724 | 17.2365 | 39.0089
4 | 69 | 73 | 73 | 75 | 133 | 101.6 | 31.2979 | 33.1122 | 33.1122 | 34.0194 | 60.3278
5 | 132 | 132 | 132 | 138 | 223 | 152.4 | 59.8742 | 59.8742 | 59.8742 | 62.5958 | 101.1511
6 | 164 | 164 | 164 | 170 | 345 | 152.4 | 74.3892 | 74.3892 | 74.3892 | 77.1107 | 156.4894
8 | 273 | 258 | 258 | 286 | 533 | 203.2 | 123.8307 | 117.0268 | 117.0268 | 129.7274 | 241.7647
10 | 454 | 436 | 436 | 485 | 1025 | 254 | 205.9309 | 197.7663 | 197.7663 | 219.9923 | 464.9322
12 | 690 | 667 | 667 | 749 | 1464 | 304.8 | 312.9788 | 302.5461 | 302.5461 | 339.7407 | 664.0593
14 | [5 empty] | 406.4
16 | [5 empty] | 406.4
18 | [5 empty] | 457.2
20 | [5 empty] | 508
24 | [5 empty] | 609.6
2500 # FLANGE WEIGHTS
|  | English | [5 empty] | Metric
Nom. | 2500 # | 2500 # | 2500 # | 2500 # | 2500 # | Nom. | 2500 # | 2500 # | 2500 # | 2500 # | 2500 #
Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG. | Pipe | WNFLG. | SO-FLG. | Thrd-FLG. | Lap-FLG. | Blind-FLG.
Size | Wt. | Wt. | Wt. | Wt. | Wt. | Size | Wt. | Wt. | Wt. | Wt. | Wt.
Inches | Lbs | Lbs | Lbs | Lbs | Lbs | mm | Kg | Kg | Kg | Kg | Kg
0.5 | 8 | 7 | 7 | 7 | 7 | 12.7 | 3.6287 | 3.1751 | 3.1751 | 3.1751 | 3.1751
0.75 | 9 | 9 | 9 | 8 | 10 | 19.05 | 4.0823 | 4.0823 | 4.0823 | 3.6287 | 4.5359
1 | 13 | 12 | 12 | 12 | 12 | 25.4 | 5.8967 | 5.4431 | 5.4431 | 5.4431 | 5.4431
1.25 | 20 | 18 | 18 | 17 | 18 | 31.75 | 9.0718 | 8.1647 | 8.1647 | 7.7111 | 8.1647
1.5 | 28 | 25 | 25 | 24 | 25 | 38.1 | 12.7006 | 11.3398 | 11.3398 | 10.8862 | 11.3398
2 | 42 | 38 | 38 | 37 | 39 | 63.5 | 19.0509 | 17.2365 | 17.2365 | 16.7829 | 17.6901
2.5 | 52 | 55 | 55 | 53 | 56 | 63.5 | 23.5868 | 24.9476 | 24.9476 | 24.0404 | 25.4012
3 | 94 | 83 | 83 | 80 | 86 | 76.2 | 42.6377 | 37.6482 | 37.6482 | 36.2874 | 39.0089
4 | 146 | 127 | 127 | 122 | 133 | 101.6 | 66.2245 | 57.6062 | 57.6062 | 55.3383 | 60.3278
5 | 244 | 210 | 210 | 204 | 223 | 152.4 | 110.6765 | 95.2544 | 95.2544 | 92.5328 | 101.1511
6 | 378 | 323 | 323 | 314 | 345 | 152.4 | 171.4579 | 146.5103 | 146.5103 | 142.428 | 156.4894
8 | 576 | 485 | 485 | 471 | 533 | 203.2 | 261.2692 | 219.9923 | 219.9923 | 213.642 | 241.7647
10 | 1068 | 925 | 925 | 897 | 1025 | 254 | 484.4367 | 419.573 | 419.573 | 406.8724 | 464.9322
12 | 1608 | 1300 | 1300 | 1262 | 1464 | 304.8 | 729.3766 | 589.6701 | 589.6701 | 572.4336 | 664.0593
14 | [5 empty] | 406.4
16 | [5 empty] | 406.4
18 | [5 empty] | 457.2
20 | [5 empty] | 508
24 | [5 empty] | 609.6